### CENWP-OP-B                                                                                                                                  18 February 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 07 of 2003, which covers the period 09 through 15 February 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 122.4 to 133.1 kcfs.  Daily project tailwater elevation averaged 11.6’ to 12.2’ msl.  Daily project forebay elevation averaged 75.0’ to 75.7’ msl.  River temperature averaged 40° F.  Daily turbidity measured 5.0’ to 7.0’ on the secchi disk.

  - Spill Bay 18, which supplies attraction flow for Bradford Island ladder, is closed 24 hours.   Spill Bay 1, which supplies attraction flow for Cascade Island ladder, is open .5’ during daylight hours.  See misc. 5.5.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 16 was out of service from 1012 until 1300 on 09 February due to a governor oil pump pressure switch problem and from 0718 until 0912 on 11 February due to governor relay work.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  During fish passage season, the units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  No AWS closures to report this week.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

Dewatering and Fish Salvage.  Biologists removed two adult clipped steelhead from A-branch diffuser pools on 11 February.

- RESEARCH.

  - NMFS Lamprey.  Tracking continues.

  - WDFW Fish Counting.  24-hr video counts at Washington Shore.

  - WDFW steelhead.  Trapping began on 10 February.

4.  FISHWAYS

  - Project biologists inspected 10-14 February this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1, PH2 | Wires removed. | Contractor work. | Will replace wires in early March. |  |
| All week | Main dam | Two wires broken | Vandalism | Will repair this winter/spring. |  |
| All week | PH2 PCC velocity | Velocity <1.5 fps. | Meter is missing | see misc. 5.1 |  |

  - Fish Ladder Temperatures.  Temperatures are not recorded in the winter.

  - Sensor Calibration.  Calibration could not be checked as there were no calibrated sensors in operation.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - Divers discovered the PH2 velocity meter was missing from the collection channel.  A new meter will be installed during the mid season dives this summer.

  - Cascade Island controls are in manual mode awaiting tailwater sensor calibration.  Electricians are awaiting parts.  B-branch is also in manual mode, pending installation of a tailwater stillwell.

  - On 24 January, the Project tailwater hard constraint decreased to 11.0’ msl for all hours.  The soft constraint went to 11.2’ msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.

  - DSM1 and DSM2 orifice lights timers have been disconnected.  Orifice lights will remain on 24 hours a day as per FPOM.

  - On 06 February, and continuing until further notice, Project spill increased to approximately 1.7 Kcfs from spill bay 1 during daylight hours.  This action was deemed necessary to attract wild winter steelhead to Cascades Island entrance while the south monolith and Bradford Island entrances are out of service.

  - A 1% violation was requested by BPA from 0850 until 1100 on 10 February and from 1200 on 14 February through the weekend.

JAMES R. MAHAR

# Operations Manager

//S//