### CENWP-OP-B                                                                                                                                     30 March 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 13 of 2003, which covers the period 23 through 29 March 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 135.2 to 237.3 kcfs.  Daily project tailwater elevation averaged 14.1’ to 19.8’ msl.  Daily project forebay elevation averaged 74.3’ to 75.2’ msl.  River temperature averaged 44 to 45° F.  Daily turbidity measured 4.5’ to 6.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are open .5’ during daylight hours in accordance to the FPP.  Spill averaged 1.6 to 2.0 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 9 was out of service from 0448 until 1724 on 26 March for semi annual maintenance.

    - Unit 10 was out of service from 0630 until 1742 on 25 March for semi annual maintenance.

    - Unit 11 was out of service from 1518 until 1630 on 26 March for STS repairs and again from 1030 until 1418 on 27 March for VBS reseating.

    - Unit 17 returned to service at 1354 on 24 March.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  During fish passage season, the units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed for cleaning this reporting week.

  - STS/VBS Inspections.  The following STS/VBS inspections were conducted this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 3/24 | 578 | Cleared under VBS in 11-B and 11-C |
| 12 | 3/24 | 543 | Cleared under VBSs |
| 13 | 3/24 | 560 | Will clear under VBSs ASAP |
| 14 | 3/24 | 552 |  |
| 15 | 3/25 | 557 |  |
| 16 | 3/25 | 567 | Will clear under VBSs ASAP |
| 17 | 3/25 | 564 |  |
| 18 | 3/25 | 614 | Will clear under VBSs ASAP |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  On 27 March, the PDS was dewatered for contractor work.

- RESEARCH.

  - NMFS Lamprey.  Tracking continues once a month.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay.

  - PSMFC.  Smolt monitoring continues.  89 steelhead, 12 salmon and one smolt slid off the end of the separator bars.

  - University of Idaho/WDFW jaw tagging.  Steelhead and spring chinook will be tagged for studies involving the tooth tangle net fishery on the Columbia.

  - USGS Juvenile Radiotracking.  USGS began installing equipment around the project.

  - WDFW Fish Counting.  16-hr video counts at Washington Shore and Bradford Island.

  - WDFW steelhead.  Trapping and tagging of winter steelhead concluded this week.

  - WES/Battelle/Mevatech Juvenile hydroacoustic monitoring.  Installing equipment.

4.  FISHWAYS

  - Project biologists inspected 23-29 March this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5fps | Meter in slowest part of channel | No response at this time. |  |
| All week | PH2 PCC | No velocity measure. | Meter is missing | See misc. 5.1 |  |
| 3/24 | B-Branch | Staff gauge reading <1.0’ | Unknown | No action taken. |  |
|  | Bonneville | Calibration | Not checked | Short staffed. |  |

  - Fish Ladder Temperatures.  Temperatures are not yet being recorded because we are awaiting new probe attachments.

  - Sensor Calibration.  Calibration was not checked this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - Divers discovered the PH2 velocity meter was missing from the collection channel.  A new meter will be installed during the mid season dives this summer.

  - On 24 January, the Project tailwater hard constraint decreased to 11.0’ msl for all hours.  The soft constraint went to 11.2’ msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.  On 17 February, BPA agreed to a hard tailwater constraint of 11.3’ msl and a soft constraint of 11.5’ msl when inflows to Bonneville are >120Kcfs.

  - Bulkheads have been installed in the PH1 orifice and sluice gates.

  - The Project is currently operating under new guidelines for one fish unit operation.  Even with the mods to the floating orifice gates, we still have some trouble maintaining differential at the south end.  We will manipulate entrance gates to try to achieve proper differential.

  - Sediment samples are still being taken as part of the Bradford Island Superfund cleanup.

  - Debarking activities in PH2 gatewells were conducted on 24 March.  We are currently looking into getting a tug to move the debris from PH2 forebay out through the navlock.

  - As of 25 March, Ms. Jennifer Sturgill is on a leave of absence for about one year.

  - DSM1 turned north at 0935 on 24 March.  Unit priority was returned to FPP criteria via a teletype on 27 March.

  - The PDS was dewatered from 0700 until 1400 on 27 March to facilitate cleaning and machining of the three-way rotating gate.

  - As of 29 March both Cascade Island and B-Branch are now operating in auto.

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  FFU is monitoring and recording their activity.

JAMES R. MAHAR

# Operations Manager

//S//