### CENWP-OP-B                                                                                                                                     13 April 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 15 of 2003, which covers the period 06 through 12April 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 186.8 to 205.6 kcfs.  Daily project tailwater elevation averaged 16.5’ to 17.5’ msl.  Daily project forebay elevation averaged 74.3’ to 75.1’ msl.  River temperature averaged 46 to 47° F.  Daily turbidity measured 3.0’ to 4.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are open .5’ during daylight hours in accordance to the FPP.  Spill averaged 2.0 to 2.1 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 9 was out of service from 0842 until 1448 on 07 April due to exciter fan problems.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  During fish passage season, the units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

FV1-1- 1559 until 1625 on 10 April.

  - STS/VBS Inspections.  No STS/VBS inspections were conducted this reporting week.

  - Dewatering and Fish Salvage.  On 10 April, biologists removed ten juvenile steelhead, 20 juvenile chinook and three sculpin from DSM1 when it was turned south for screen sweep repairs.

- RESEARCH.

  - NMFS Lamprey.  Tracking continues once a month.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace.

  - ODFW Steelhead.  Trapping 1% of the summer steelhead continues two days a week.

  - PSMFC at DSM1.  Continuous PIT tag interrogation continues.  GBT and monitoring began 07 April.

  - PSMFC at the SMF.  Five kelts (four alive and one dead) were stuck on the separator bars.  Monitoring personnel observed 134 steelhead, 41 salmon, nine unknown salmonids and 41 smolt slide over the separator bars.

  - University of Idaho.  Adult tracking tagging and tracking continue.

  - University of Idaho/WDFW jaw tagging.  Steelhead and spring chinook will be tagged for studies involving the tooth tangle net fishery on the Columbia.

  - USGS Juvenile Radiotracking.  USGS still installing equipment around the project.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

  - WES/Battelle/BAE systems Juvenile hydroacoustic monitoring.  Installing equipment.

4.  FISHWAYS

  - Project biologists inspected 06-12 April this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5fps | Meter in slowest part of channel | No response at this time. |  |
| All week | PH2 PCC | No velocity measure. | Meter is missing | See misc. 5.1 |  |
| 4/9, 4/11 | Weir 37 | Staff gauge reading >1.0’ | Unknown | No action taken. |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Kelvin.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 4/6 | 281.8 | 281.8 |
| 4/7 | 281.9 | 281.8 |
| 4/8 | 282.0 | 281.9 |
| 4/9 | 282.2 | 282.2 |
| 4/10 | 282.5 | 282.4 |
| 4/11 | 282.6 | 282.6 |
| 4/12 | 282.8 | 282.7 |

  - Sensor Calibration.  Calibration was checked on 09 April this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - Divers discovered the PH2 velocity meter was missing from the collection channel.  A new meter will be installed during the mid season dives this summer.

  - On 24 January, the Project tailwater hard constraint decreased to 11.0’ msl for all hours.  The soft constraint went to 11.2’ msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.  On 17 February, BPA agreed to a hard tailwater constraint of 11.3’ msl and a soft constraint of 11.5’ msl when inflows to Bonneville are >120Kcfs.

  - The Project is currently operating under new guidelines for one fish unit operation.  Even with the mods to the floating orifice gates, we still have some trouble maintaining differential at the south end.  We will manipulate entrance gates to try to achieve proper differential.

  - Cascade Island is mostly operating in Auto.  FV5-3 (conduit supply) is still in manual due to a faulty transducer.

  - Debarking of PH2 gatewells occurred on 07 April.  A request for a contract for a tug to remove debris from PH2 forebay has been made.

  - Sediment samples are still being taken as part of the Bradford Island cleanup.  Dive operations concluded on 08 April.

  - The small screen sweep at DSM1 went out of service at 2318 on 09 April.  The sweep brush arm jammed and would not break free.  DSM1 was turned south and the bulkhead installed from 1117 until 1425 on 10 April to facilitate repairs to the small screen sweep.

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  FFU is monitoring and recording their activity.

JAMES R. MAHAR

# Operations Manager

//S//