### CENWP-OP-B                                                                                                                        22 September 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 38 of 2003, which covers the period 14 through 20 September 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 80.7 to 100.7 kcfs.  Daily project tailwater elevation averaged 7.3’ to 9.3’ msl.  Daily project forebay elevation averaged 75.8’ to 76.1’ msl.  River temperature averaged 64 to 66° F.  Daily turbidity measured 5.3’ to 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are open .5’ from 0530 until 1930 each day.  Spill averaged 2.2 to 2.6 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Units 2 through 6 remain out of service due to crane rail replacement.

    - Unit 7 remains out of service for its five year overhaul.

    - Unit 8 remains out of service due to crane rail replacement.

    - Unit 9 was out of service from 1101 until 1309 on 15 September for STS installation

    - Unit 10 was out of service from 0824 until 1031 on 15 September for STS installation.

    - Unit 13 was out of service from 1140 until 1530 on 17 September for STS connector repairs.

    - Unit 14 remains out of service for its four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   See Const. 5.3

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV3-9 was closed for cleaning from 0719 until 0732 on 15 September.

    - FG3-3 went out of service at 0700 on 13 September.  The diffuser is binding mechanically.  FG3-4 will be opened in place of FG3-3, when necessary.

    - FG3-4 was open from 0840 on 19 September until 0710 on 20 September.

  - STS/VBS Inspections.  No STS/VBS inspections were conducted this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH.

  - CRITFC.   Sampling of chinook, sockeye, and coho continues until 31 October.

  - NMFS Lamprey.  Trapping, tagging and tracking continue.

  - ODFW Steelhead.  Trapping continues one to two days a week.

  - PSMFC at the SMF.  Three steelhead and 10 salmon  slid over the separator bars.

  - University of Idaho.  Adult tracking tagging and tracking continues.

  - WDFW Pink DNA.  WDFW is taking DNA samples from pinks collected in the AFF this week.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

  - WDFW Tule counter.  Visual counts continue at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 14 through 20 September this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week. | PH1 PCC | Velocity <1.5fps | Meter in slowest part of channel | No response at this time. |  |
| All week | PH2 PCC | No velocity measure. | Logic board was short circuited | Sending in to mfr for repair |  |
| All week | PH1 ITS | 7A closed. | Crane rail work | 8B opened. See const. 5.2.1 |  |
| 9/14-15, 9/19 | Weir 37 | Reading >1.0’ | Fish clogging up the grate | Operators to blow off screen. |  |

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius this week.  http://students.washington.edu/kyle/temptable.jpg   (295.37K = 22.22C= 72F)

| Date | WA Shore | Bradford Is. | ##### AFF exit |
| --- | --- | --- | --- |
| 9/14 | 19.65 | 19.65 | 19.65 |
| 9/15 | 19.75 | 19.65 | 19.75 |
| 9/16 | 19.55 | 19.45 | 19.55 |
| 9/17 | 19.15 | 19.05 | 19.05 |
| 9/18 | 19.15 | 19.05 | 19.15 |
| 9/19 | 19.35 | 19.25 | 19.25 |
| 9/20 | 19.15 | 19.05 | 19.05 |

  - Sensor Calibration.  Calibration was checked on 19 September this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - PH 2 Corner Collector-  nothing to report this week.

  - PH 1 Crane Rail Replacement- started on 01 August and will continue until 16 December.

    - As a safety precaution, chain gate 7A has been closed (8A to compensate) and the end gate will be closed during the hours of 0530 until 1900 for the contractors working over the ITS.  The end gate will be opened each evening to flush fish.

    - PH1 priority is Unit 10 then Unit 9 with STSs.  The ITS will be opened during unit operation and allowed to run for not less than four hours after the units have been shutdown (to flush fish that may have been attracted into PH1 forebay).

    - PH1 ITS, Unit 9 and Unit 10 operations summary

  - September- Units 9 and 10 in operation as the priority units.  See misc. 6.1

  - PH2 AWS Trashrack Mods.

    - Both fish units were placed on standby from 2112 until 2232 on 16 September.  This was to facilitate a preliminary ROV camera inspection of the debris in front of the fish unit trashracks.

    - Unit 18 was on standby from 2115 until 2232 on 16 September to facilitate the ROV inspection of the Fish Unit trashracks.

- MISCELLANEOUS

  - At 0936 on 12 September, RCC issued a teletype directing Bonneville to run PH1 units as the priority.  This action was taken in an attempt to more evenly distribute the high numbers of salmon going through the Washington Shore fishway and relatively few going through Bradford Island.

  - At 1255 on 14 September, DSM2 screen cleaner #2 broke a chain.  It returned to service at 1152 on 15 September.

JAMES R. MAHAR, P.E.

Operations Manager

//S//