### CENWP-OP-B                                                                                                                        12 October 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 41 of 2003, which covers the period 05 through 11 04 October 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 77.2 to 111.7 kcfs.  Daily project tailwater elevation averaged 7.4’ to 10.7’ msl.  Daily project forebay elevation averaged 74.5’ to 75.5’ msl.  River temperature averaged 62 to 64° F.  Daily turbidity measured 6.0’ to 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascade Island and Bradford Island fishways respectively, are open .5’ from 0530 until 1930 each day.  Spill averaged 2.3 to 2.5 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Units 2 through 6 remain out of service due to crane rail replacement.

    - Unit 7 remains out of service for its five year overhaul.

    - Unit 8 remains out of service due to crane rail replacement.

    - Unit 11 was out of service from 0929 until 1100 on 06 October for STS repair.

    - Unit 14 remains out of service for its four year overhaul.

    - Unit 16 was out of service from 1900, 06 October until 1135, 07 October for Kaplan piping tightening.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed for cleaning this reporting week.

  - STS/VBS Inspections.  The following STS/VBS inspections were conducted this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 10/06 | 672 | Rip in STS 4”X70”. Replaced with #12 spare STS |
| 12 | 10/06 | 553 |  |
| 13 | 10/06 | 396 |  |
| 14 | 8/11 | 314 | Pulled for unit overhaul |
| 15 | 10/06 | 324 |  |
| 16 | 10/06 | 632 |  |
| 17 | 10/06 | 677 |  |
| 18 | 10/06 | 677 |  |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH.

  - CRITFC.   Sampling of chinook, sockeye, and coho continues until 31 October.

  - ODFW Steelhead.  Trapping continues one to two days a week.

  - PSMFC at the SMF.  One adult steelhead, 19 fallback salmon, and one unknown salmonid slid off the separator bars.

  - University of Idaho.  Adult tracking tagging and tracking continues.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 05 through 11 October this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| 10/5, 10/7-11 | PH1 PCC | Velocity <1.5fps | Meter in slowest part of channel | No response at this time. |  |
| All week | PH2 PCC | No velocity measure. | Logic board was short circuited | Sending in to mfr for repair |  |
| All week | FG3-3, FG3-4 | Diffuser out of service | Mechanical binding. | FG3-4 to compensate. Repairs this winter. |  |

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius this week.  http://students.washington.edu/kyle/temptable.jpg   (295.37K = 22.22C= 72F)

| Date | WA Shore | Bradford Is. | ##### AFF exit |
| --- | --- | --- | --- |
| 10/05 | 18.75 | 18.65 | 18.65 |
| 10/06 | 18.65 | 18.65 | 18.65 |
| 10/07 | 18.55 | 18.55 | 18.55 |
| 10/08 | 18.45 | 18.35 | 18.45 |
| 10/09 | 18.25 | 18.05 | 18.15 |
| 10/10 | 17.95 | 17.95 | 17.95 |
| 10/11 | 17.75 | 17.55 | 17.65 |

  - Sensor Calibration.  Calibration was not checked this week due to training of the new biologist.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - PH 2 Corner Collector-  October 15th will be the test date for the bulkhead and chute.

  - PH 1 Crane Rail Replacement- started on 01 August and will continue until 16 December.

    - As a safety precaution, chain gate 7A (8B to compensate) and the ITS end gate are closed during construction.  Please see 5.2.3 for ITS closure times.

    - When Units 9 and 10 are in operation, the ITS will be opened and allowed to run for not less than four hours after the units have been shutdown (to flush fish that may have been attracted into PH1 forebay).

    - PH1 ITS, Unit 9 and Unit 10 operations summary

- October- ITS closed from 0530 until 1900.

- October- ITS closed from 0525 until 0805.  Units 9 and 10 in service from 0805 until 2110.

- October- ITS closed from 0630 until 1730.

- October- ITS closed from 0530 until 1704.  Units 9 and 10 in service at 1704.

- October- Units 9 and 10 to standby at 0200.  ITS closed from 0530 until 1105.  Units 9 and 10 in service from 1106 until 1212.

- October- ITS closed from 0607 until 1130.  Unit 10 in operation at 1500.

  - Adult PIT tag detection (vertical slots).  The project management plan is out for review.

  - High Flow PIT tag detectors for B2CC.  50% P&S out.  Comments due by 20 October.

  - Main dam excavation work.  Excavation to begin 20 October.  Kiewit expects to be done by 25 October.

  - PH2 FGE/VBS mods.  BCOE comments due by 15 October.

JAMES R. MAHAR, P.E.

Operations Manager

//S//