### CENWP-OP-B                                                                                                                        24 November 2003

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 47 of 2003, which covers the period 16 through 22 November 2003.

- OPERATION SUMMARY.

  - Daily river flow averaged 117.3 to 148.0 kcfs.  Daily project tailwater elevation averaged 11.5’ to 13.5’ msl.  Daily project forebay elevation averaged 73.3’ to 76.0’ msl.  River temperature averaged 46 to 48° F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island fishways respectively, are open .5’ from 0530 until 1930 each day.  Spill averaged 2.3 to 2.7 kcfs.

  - Unit operation

    - Unit 1 remains out of service for turbine rehab.

    - Units 2 through 4 remain out of service due to crane rail replacement.

    - Unit 11 remains out of service due to an emergency shutdown on 17 October.

    - Unit 14 was out of service from 0349 on 17 November until 1045 on 18 November due to a servo oil leak.

    - Unit 17 was out of service from 1128 until 1330 on 17 November for STS repairs.

    - Unit 18 was out of service from 1336 until 1603 on 17 November for STS repairs.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.   F1 was out of service from 2245 on 22 November until 0200 on 23 November due to a problem with the field flash contactor.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

FV1-1- closed for cleaning from 0740 until 0758 on 17 November and from 0730 until 0744 on 22 November.

FV3-9- closed for cleaning from 0705 until 0724 on 17 November, from 1254 until 1308 on 20 November, and from 0745 until 0820 on 22 November.

FV6-9- closed for cleaning from 0816 until 0830 on 17 November.

  - STS/VBS Inspections.  The following STS/VBS inspections were conducted this reporting week.

| 16 | 11/17 | 968 |  |
| --- | --- | --- | --- |
| 17 | 11/17 | 1009 | Repaired rip in “A” slot |
| 18 | 11/17 | 1008 | Repaired several rips in “A” slot |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.   Upcoming activities include-

    - DSM2 coming out of service on 01 December.

    - Two mile pipe inspection on 02 December.

    - Cascades Island dewater on 03 December.

- RESEARCH.

  - WDFW Fish Counting.  16-hr video counts at Washington Shore and Bradford Island.

  - WDFW Chum.  Chum trapping and tagging continues.

4.  FISHWAYS

  - Project biologists inspected 16 through 22 November this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5fps | Meter in slowest part of channel | No response at this time. |  |
| 11/17, 11/20-22 | PH2 PCC | Velocity <1.5fps |  | No response |  |
| All week | FG3-3, FG3-4 | FG3-3 OOS | Mechanical binding. | FG3-4 to compensate. |  |
| 11/18 | BI weirs | Reading <1.0’ over the weir. | AWS trashracks need cleaned. | Trash raking underway |  |

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Kelvin this week.  http://students.washington.edu/kyle/temptable.jpg   (295.37K = 22.22C= 72F)

| Date | WA Shore | Bradford Is. |
| --- | --- | --- |
| 11/16 | 283.2 | 283.2 |
| 11/17 | 282.8 | 282.9 |
| 11/18 | 282.8 | 282.9 |
| 11/19 | 282.8 | 282.9 |
| 11/20 | 282.6 | 282.7 |
| 11/21 | 282.3 | 282.4 |
| 11/22 | 282.2 | 282.2 |

  - Sensor Calibration.  Calibration was checked on 22 November this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - PH 2 Corner Collector- Avian anchors to be installed.

  - PH 1 Crane Rail Replacement- started on 01 August and will continue until 16 December.

    - As a safety precaution, chain gate 7A (8B to compensate) is closed during construction.

- MISCELLANEOUS

  - Per a teletype sent on 17 November, Project tailwater will have a soft constraint of 11.4’ to 11.7’ msl between the hours of 0700 until 1900.  This constraint is for chum spawning habitat located below the dam.

  - The Project violated the soft tailwater constraint of 11.7’ msl on 22 November.  Tailwater was as high at 11.9’ msl.

  - On 22 November, the Project has a 1% violation at the request of BPA.

  - Project Fisheries is working with Bonneville Rangers in submitting a grant proposal for the Trout Unlimited Embrace A Stream grant.  We are looking at weed removal, re-vegetation, and in stream restoration at Bass Lake.

JAMES R. MAHAR, P.E.

Operations Manager

//S//