### CENWP-OP-B                                                                                                                                     01 March 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 09 of 2004, which covers the period 22 through 28 February 2004.

- OPERATION SUMMARY.

  - Daily river flow averaged 121.1 to 159.9 kcfs.  Daily project tailwater elevation averaged 12.1’ to 14.4’ msl.  Daily project forebay elevation averaged 74.2’ to 75.3’ msl.  River temperature averaged 38° F.  Daily turbidity measured 3.8 to 5.0 on the secchi disk.

  - Spill Bays 1 and 18 will remain closed until 01 March as per TMT.  Spill averaged 0 kcfs.

  - Unit operation.  PH2 became the priority powerhouse on 24 February.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 2 was out of service from 0755 until 1258 on 23 February for transducer installation.

    - Unit 3 was out of service from 1254 until 1418 on 23 February for transducer installation.

    - Unit 7 was out of service from 1416 until 1638 on 23 February for transducer installation.

    - Unit 9 was out of service from 1618 until 1656 on 23 February for trashrack raking and transducer installation.

    - Unit 10 remains out of service.

    - Unit 11 remains out of service.

    - Unit 12 was out of service from 1110 until 1329 on 26 February for STS installation.

    - Unit 13 was out of service from 0911 until 1118 on 26 February for STS installation.

    - Unit 14 was out of service from 1143 until 1400 on 25 February for STS installation.

    - Unit 15 was out of service from 1405 until 1633 on 25 February for STS installation.

    - Unit 16 was out of service from 0756 until 0858 on 26 February for STS installation.

    - Unit 17 remains out of service for VBS modifications.

    - Unit 18 was out of service from 1058 on 23 February until 1500 on 25 February for wicket gate packing.  Unit 18 was also out of service from 0636 until 0750 on 26 February for STS installation.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F1 was out of service from 0712 on 23 February until 1720 on 24 February to facilitate trashrack removal.  F1 went out of service at 2120 on 28 February due to a governor failure.

    - F2 returned to service at 1348 on 25 February.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures. No AWS valves were closed this reporting week.

  - STS/VBS Inspections.  The following STSs were installed this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 |  |  | OOS |
| 12 | 2/26 |  |  |
| 13 | 2/26 |  |  |
| 14 | 2/26 |  |  |
| 15 | 2/25 |  |  |
| 16 | 2/25 |  |  |
| 17 |  |  | OOS VBS Modifications |
| 18 | 2/26 |  |  |

Table 1.  STS Installation Dates.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities this reporting week.

- RESEARCH.

  - Battelle FGE testing.  Transducer installation at PH1 nearly complete.

  - CRITFC.  Scheduled to start in mid-March.

  - ERDC TDG.  Sensors were installed below the B2CC on 17 February.

  - NOAA FISH lamprey.  Lamprey ladder installation in Spring.  Meeting 10 March to discuss the ladder design and placement at Bonneville.

  - NOAA FISH NaCl.  Maintaining the saltwater facility though no research is scheduled this season.

  - PSMFC SMF.  Preparing to start 02 March.

  - PSMFC PIT tag.  Testing an antenna for the serpentine sections of the fishways.

  - Spring Creek Hatchery.  First release scheduled for 01 March.  Spill to begin on 02 March.

  - USGS FPE testing.  Radio telemetry equipment to be installed on the Project throughout February.

  - WDFW Fish Counting.  16-hr video counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 23-27 February this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel. | No action taken. This is a normal condition. |  |
| 2/23-24 | PH2 PCC | Velocity <1.5fps | Signal not transmitting between sensor and computer. | Electricians working on finding cause and possible repair. |  |
| All week | FG3-3, FG3-4 | Not in correct position for TW | FG3-3 not controlling. FG3-4 has a bent shaft. | Electricians working on FG3-3. Mechanics looking at FG3-4. May leave diffuser open until winter 04/05 |  |
| 2/23-24 | PH2 monoliths | Head differential low | Fish units OOS for trashrack dive. |  |  |

  - Fish Ladder Temperatures.  Temperatures are not recorded during winter maintenance season.

  - Sensor Calibration.  Calibration was checked on 27 February.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Fishway Status.

    - DSM2 returned to service at 1600 on 25 February.  The airburst is run in manual every six hours.  Debris loading will be monitored.

    - DSM1 remains out of service.

    - B2CC getting outfitted with antennas.  The corner collector will be used during the second Spring Creek Release.

    - Navlock dewatering scheduled for 06-08 March.

- CONSTRUCTION

  - PH 2 Corner Collector- Antennas being installed in the gate slot filler panel.

  - PH 2 Corner Collector Hi-Q PIT tag detector- Prototype still planned for installation in 2004.

  - PH2 Corner Collector Avian Wires- Avian wire installed.

  - Unit 17 VBS mods.  From the hours between 1200-1800, after 1 March 2004 until completion, no work such as concrete saw cutting, bush and vibro-hammering may be done inside the gatewells of unit 17 at PH2.  Between 0000-1200 and 1800-2400 hours, the contractor may complete work inside the gatewells with the associated equipment and construction techniques dealing with concrete saw cutting, bush and vibro-hammering.

  - B2 Follow-on.  The contractors finished the airburst installation.  Due to problems with the I/O hardware, the system will be ran in manual every six hours (or more often if necessary) until repairs can be made.

- MISCELLANEOUS

  - Per a teletype sent on 18 December, Project tailwater will have a hard constraint of 11.8’ and a soft constraint of 11.8’ to 12.1’ between the hours of 0700 until 1700.  This constraint is for chum spawning habitat located below the dam.

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.

  - BPA requested a 1% violation from 1320 until 1515 on 25 February.

  - TIES were installed on 20 February.

  - On the morning of 27 February, an oil sheen was found in gatewell slot 11C.  Operators shut down all Unit 11 gatewell orifices until the source of the oil could be located.  It was estimated to be about .1 gallons of oil in slots 11A and 11C.  Sorbent sheets were placed in both slots and left over the weekend.  As much of the sheen as possible was removed.  The source of the oil could not be determined and by 01 March all gatewell orifices were back in normal operation.

  - The hydro cannons at the SMF are not operational at this time.  There is a break in the water lines.  The Project is working on repairs.  Please see memo sent out by Project Fisheries on 02 March.

JAMES R. MAHAR, P.E.

Operations Manager

//S//