### CENWP-OP-B                                                                                                                                     11 May 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 19 of 2004, which covers the period 02 May through 08 May 2004.

- OPERATION SUMMARY.

  - Daily river flow averaged 185.4 to 250.2 kcfs.  Daily project tailwater elevation averaged 14.7’ to 18.7’ msl.  Daily project forebay elevation averaged 75.1’ to 75.8’ msl.  Daily river temperature averaged 53 to 54° F.  Daily turbidity measured 3.5 to 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 87.5 to 95.2 kcfs.   See misc. 6.2

  - Unit operation.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 15 went to manual 3D cam adjustment at 0933 on 05 April.  The cam was automatically adjusting and draining power which led to a governor lock up and complete loss of control.  New modules are on order.

    - Unit 16 went out of service at 1010 on 03 May for air cylinder brake repair.

    - Fish Unit 1 (FI) was out of service from 0748 until 0814 on 04 May for trash raking.

    - Fish Unit 2 (F2) was out of service from 0706 until 0748 on 04 May for trash raking.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed this reporting week.

  - STS/VBS Inspections.  No STSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

Unit 16 Tail logs.   No fish were found on 6 May.

- RESEARCH.

  - Battelle/BAE Systems FGE testing.  Hydroacoustic installation complete.  Data collection continues.

  - Battelle/BAE Systems Gap Loss Testing.  Data collection began 06 May.

  - CRITFC.  Sampling twice a week.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace.

  - NOAA FISH lamprey.  Lamprey ladder installation in May.

  - PSMFC SMF.  Six steelhead and one salmon slid over the separator bars this week.  Approximately 670 clipped yearling chinook and 290 clipped steelhead were held for USGS. High mortality occurred on 1 May when 68 smolts were killed due to fish lift failure and loss of flushing water to the lift.   See misc. 6.4 PSMFC PIT tag.  Testing an antenna for the serpentine sections of the fishways.

  - USGS FPE testing.  Installation of Radio telemetry equipment complete.  First tagged fish released on 29 April.

  - University of Idaho.  Sampling daily in the AFF.

  - Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 02 May through 08 May this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel. | This is a normal condition. |  |
| All week | FG3-4 | Incorrect position for TW | Bent shaft | No action taken. |  |
| 5/2-5/3, 5/5-5/8 | PH2 PCC | Velocity < 1.5 fps | Unknown |  |  |
| 5/5-5/7 | Weirs 37/38 | Weirs reading < > 1.0’ | Unknown | No action taken. |  |
| All week | Spill bays 1 and 18 | Improper spill gate opening | Gate hoist malfunction | See misc. 6.2 |  |

  - Fish Ladder Temperatures.  (Computer problems.  Will be reported next week.)  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 4/25 |  |  |
| 4/26 |  |  |
| 4/27 |  |  |
| 4/28 |  |  |
| 4/29 |  |  |
| 4/30 |  |  |
| 5/1 |  |  |

  - Sensor Calibration.  Calibration was checked on 08 May this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Fishway Status.

    - DSM1 remains out of service.

    - On 23 April, the CI fish ladder went to manual due to computer problems.  The ladder remained in criteria.

- CONSTRUCTION

  - PH 2 Corner Collector Hi-Q PIT tag detector- Prototype antenna construction started on Cascades Island.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.

  - SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  The Project is working on repairs.

  - Adult PIT tag exit detectors.  Current schedule is set for installation in both ladders for Winter 04/05.

  - Head Gate Delivery.  Off loading of headgates at PH1 is scheduled for 07 June 2004.

  - PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.

  - On 19 April gate hoists for spillbays 1 and 18 were found to be damaged and a safety hazard.  Bays 1 and 18 were dogged off at 2 dogs (2.9 feet).  On 20 April, the bays were dropped to one dog (one foot) in an effort to reduce turbulence at the fishway entrances.  Per a 21 April teletype, spill will be compensated through adjacent bays 2 and 17 and through 3 and 16 in one foot increments.

  - On 30 April, the project received a teletype for a hard constraint forebay elevation of 75-76.5’ msl from 0600 on 4 May until 1800 on 6 May.  This is for the tribal treaty gillnet fishery.

  - While repairs to the fish lift were being conducted, the flushing water was inadvertently shut off.    Will work with PSMFC and Project personnel to assure this does not happen in the future.

JAMES R. MAHAR, P.E.

Operations Manager

//S//