### CENWP-OP-B                                                                                                                                     23 May 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 21 of 2004, which covers the period 16 May through 22 May 2004.

- OPERATION SUMMARY.

  - Daily river flow averaged 208.3 to 255.8 kcfs.  Daily project tailwater elevation averaged 16.2’ to 18.9’ msl.  Daily project forebay elevation averaged 75.4’ to 75.8’ msl.  Daily river temperature averaged 55 to 56° F.  Daily turbidity measured 4.5 to 6.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 93.8 to 96.7 kcfs.   See misc. 6.2

  - Unit operation.

    - Unit 0 was out of service from 0530 until 1508 on 18 May for gland water pipe repair.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 15 went to manual 3D cam adjustment at 0933 on 05 April.  The cam was automatically adjusting and draining power which led to a governor lock up and complete loss of control.  New modules are on order.

    - 1% violation - Units 14, 16, and 18 on 20 May for STS inspections.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed this reporting week.

  - STS/VBS Inspections.  The following STS/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 12 13 14 15 16 17 18 | 5/19 5/25 5/25 5/20 4/26 5/20 5/10 5/20 | 558 550 537 465 567 136 777 503 | Will inspect ASAP C-slot covered for Gap Loss test. Will video when test is complete. |

Table 1.  STS Installation Dates.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH.

  - Battelle/BAE Systems FGE testing.  Data collection continues.

  - Battelle/BAE Systems Gap Loss Testing.  Data collection continues through 3 June.

  - CRITFC.  Sampling twice a week.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace will continue on 6/28-7/2.

  - NMFS.  320-clipped yearling chinook were collected for NMFS researchers during the week.

  - NOAA FISH lamprey.  Lamprey ladder installation in May.

  - PSMFC SMF.  Eleven steelhead and one salmon slid over the separator bars this week.  Two kelts were stuck on separator bars and released alive.

  - USGS FPE testing.  Installation of Radio telemetry equipment complete.  First tagged fish released on 29 April.  PSMFC collected 657-clipped yearling chinook and 630-clipped steelhead for USGS testing.

  - University of Idaho.  Sampling daily in the AFF.

  - Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 16 May through 22 May this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel. | This is a normal condition. |  |
| All week | FG3-4 | Incorrect position for TW | Bent shaft | No action taken. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | Unknown |  |  |
| All week | SUE, SDE | Tail water gate < 13’ | Unknown | Recalibration |  |
| 5/16-20 | Spill bays 1 & 18 | Improper spill gate opening | Gate hoist malfunction | Repaired on 20 May |  |
| 5/18 | Weirs 37 | Weirs reading <1.3’> | Unknown | Operators to adjust bleed off valve |  |
| 5/16-17 | UMT Staff gauge | Weirs reading <1.3’> | Not yet in shad passage mode | TR submitted | 04-19135 |
| 5/16-17 | A and B Branches | Weirs reading <1.3’> | Not yet in shad passage mode | TR submitted | 04-19135 |

  - Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/16 | 57.9 | 58.0 |
| 5/17 | 57.9 | 58.0 |
| 5/18 | 57.9 | 58.1 |
| 5/19 | 57.9 | 57.9 |
| 5/20 | 58.3 | 58.3 |
| 5/21 | 58.0 | 58.1 |
| 5/22 | 57.7 | 57.8 |

  - Sensor Calibration.  Calibration was checked on 22 May this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Fishway Status.

- CONSTRUCTION

  - PH 2 Corner Collector Hi-Q PIT tag detector- Prototype antenna construction started on Cascades Island.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.

  - SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  The Project is working on repairs.

  - Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

  - Head Gate Delivery.  Off loading of headgates at PH1 is scheduled for 07 June 2004.

  - PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.

  - On 18 May at 1006, spill bay 18 returned to normal operation according to FPP.  On 20 May at 1000, spill bay 1 returned to normal operation according to FPP.

  - On 16 May, a new Teletype indicating an increase to 120% TDG for the evening to 135 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S//