### CENWP-OP-B                                                                                                                                     9 June 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 23 of 2004, which covers the period 30 May through 5 June 2004.

- OPERATION SUMMARY.

  - Daily river flow averaged 269.9 to 308.9 kcfs.  Daily project tailwater elevation averaged 20.1’ to 22.1’ msl.  Daily project forebay elevation averaged 74.9’ to 75.9’ msl.  Daily river temperature averaged 56 to 58° F.  Daily turbidity measured 3.0 to 4.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 92.8 to 105.1 kcfs.

  - Unit operation.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 3 went out of service from 1330 until 1438 on 02 June to replace the turbine bearing low flow indicator.

    - Unit 5 went out of service from 0430 on 2 June until 1403 on 3 June for annual maintenance.

    - Unit 15 went to manual 3D cam adjustment at 0933 on 5 April.  New modules are on order.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed this reporting week.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH.

  - Battelle/BAE Systems FGE testing.  Data collection continues.

  - Battelle/BAE Systems Gap Loss Testing.  Test ended on 4 June.

  - CRITFC.  Sampling twice a week.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace will continue on 28 June through 2 July.

  - NMFS.  No fish were collected for NMFS researchers during the week.

  - NOAA FISH lamprey.  Lamprey ladder installation began 24 May.

  - PSMFC SMF.  Eight steelhead and one salmon slid over the separator bars this week.  Two kelts were stuck on the separator bars and released alive.

  - USGS FPE testing.  Last fish release occurred on 3 June for the spring study.  Summer study to begin 20 June.  PSMFC collected 165-clipped yearling chinook and 400-clipped steelhead for USGS RT testing.

  - University of Idaho.  Sampling daily in the AFF.

  - Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 30 May through 5 June this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel | This is a normal condition. |  |
| All week | FG3-4 | Incorrect position for TW | Bent shaft | No action taken. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | No acoustic sensor | Will repair during winter 04/05 |  |
| 5/30 and 6/1 | BI weir | Weir reading 1.0 and 1.3 | Unknown | Operators to adjust |  |
| 6/5 | Spillbay 14 | Gate position > 1.5 | Limit switch. | Electricians called See Misc 6.2 |  |
| 6/5 | Weir 37 | Weir reading >1.3’ | Shad | Operators adjusted valve See Misc 6.3 |  |
| 6/5 | Gate 64 | > 8.4 submergence | Breaker tripped | Operators restored connection. Controlling properly. |  |
| 5/30-6/2 and 6/4 -5 | Cascade Island | In manual | Computer software issue | TR submitted See 4.6.1 | 04-21382 |
| 6/1 | DSM2 | ERG tripped | Debris loading | Switched airburst to operate hourly. See 4.6.2 |  |

  - Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/30 | 58.6 | 58.6 |
| 5/31 | 58.8 | 58.8 |
| 6/1 | 58.9 | 59.0 |
| 6/2 | 59.4 | 59.5 |
| 6/3 | 59.9 | 60.0 |
| 6/4 | 60.3 | 60.4 |
| 6/5 | 60.3 | 60.4 |

  - Sensor Calibration.  Calibration was checked on 5 June this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Fishway Status.

    - Cascade Island has not been properly controlling in Auto most of this week due to a software issue.    TR has been submitted.

    - At the DSM2, the ERG (emergency relief gate) opened at 0220 and closed at 0235 on 1 June due to a high channel elevation.  The airburst system was set to operate hourly instead of every 3 hours due to higher debris loading on the dewatering screen.

- CONSTRUCTION

  - PH 2 Corner Collector Hi-Q PIT tag detector- Prototype antenna construction started on Cascades Island.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.  See Misc. 6.4

  - SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  The Project is working on repairs.    See Misc 6.5

  - Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

  - Head Gate Delivery.  Off loading of headgates at PH1 is scheduled for 7 June 2004.

  - PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - Sea lions and harbor seals have not been observed in the tailrace of both powerhouses and the spillway since 26 May.

  - Spillbay 14 was not controlling properly from 0410 until 0930 on 5 June.  Electricians were called in to repair the limit switch.   During that time, spillbay 14 was open 3.7 feet and the four adjacent bays were used to compensate and maintain 75 kcfs total spill.

  - Shad appear to be clogging the bleed off valve for weir 37.  Operators to blow air through the screen twice daily and structural crew to rake on Monday’s and Thursday’s if needed.

  - PIT antenna scheduled for delivery at PH 2 forebay on 24 June.

  - Repairs to the avian canon are scheduled for completion by the end of June.  Wildlife services will conduct full time hazing activities until 26 June.

  - The Project had released approximately 10 gallons of turbine oil into the river by the old navigation lock on 5 June.  Once the final report is available, I will send out an official memorandum with the details.

JAMES R. MAHAR, P.E.

Operations Manager

//S//