### CENWP-OP-B                                                                                                                                     12 July 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 28 of 2004, which covers the period 4 July through 10 July 2004.

- OPERATION SUMMARY.

  - Daily river flow averaged 176.8 to 203.8 kcfs.  Daily project tailwater elevation averaged 14.3’ to 15.6’ msl.  Daily project forebay elevation averaged 74.0’ to 75.4’ msl.  Daily river temperature averaged 65° F.  Daily turbidity measured 4.0 to 6.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 50.0 to 97.0 kcfs.   BiOp versus 50kcfs testing started on 17 June.

  - Unit operation.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 15 remains on manual 3D cam adjustment.  New modules are on order.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed this reporting week:

    - FV 3-7 was closed for cleaning from 1129 until 1146 on 6 July and from 1056 until 1145 on 7 July.

    - FV 3-9 was closed for cleaning from 1309 until 1330 on 6 July and from 1315 until 1345 on 7 July.

  - STS/VBS Inspections.    No inspections were conducted this week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH.

  - Battelle/BAE Systems FGE testing.  Data collection continues.

  - CRITFC.  Sampling twice a week.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA FISH lamprey.  Lamprey ladder installation complete.

  - PSMFC SMF.  No fish were observed sliding over the separator bars this week.

  - USGS FPE testing.  Releasing of radio tagged fish continues.   Last fish release scheduled for 31 July.  PSMFC collected 1,120 subyearling chinook for USGS RT testing.

  - University of Idaho.  Sampling daily in the AFF.

  - Wildlife Services/Avian Abatement.  Birds were hazed this reporting week with rockets, cracker shells, and 15mm pyrotechnics.  None were lethally taken.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

4.  FISHWAYS

  - Project biologists inspected 4 July through 10 July this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel | This is a normal condition. |  |
| All week | FG3-4 | Incorrect position for TW | Bent shaft | No action taken. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | No acoustic sensor | Will repair during winter 04/05 |  |

  - Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| Date | Wash. Shore | Bradford Is. | ##### AFF exit |
| --- | --- | --- | --- |
| 7/4 | 67.7 | 67.8 | 67.7 |
| 7/5 | 67.6 | 67.8 | 67.6 |
| 7/6 | 68.1 | 68.2 | 68.1 |
| 7/7 | 68.0 | 68.0 | 68.0 |
| 7/8 | 67.9 | 67.9 | 67.8 |
| 7/9 | 67.9 | 67.9 | 67.9 |
| 7/10 | 67.9 | 68.0 | 67.9 |

  - Sensor Calibration.  Calibration was checked on 7 July this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Fishway Status.

    - FV 4-3 and FV 4-4 went to manual at 1421 on 8 July due to a bad ladder elevation sensor.  FV 4-4 returned to auto on 9 July.

    - Washington and Cascades Island ladders were operated out of criteria from 1207 until 1324 on 10 July.   See Misc 6.2

- CONSTRUCTION

  - PH 2 Corner Collector Hi-Q PIT tag detector.  If feasible, the prototype antenna will then be constructed into the existing channel during the in-water work period during FY05.

  - SMF hydrocannons.  The hydro cannons at the SMF are not operational at this time.  Repairs to the avian cannon are scheduled for completion by 15 July.  Wildlife services will conduct full time hazing activities until 17 July or until the hydro cannon is operational.

  - Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

  - PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - On 17 June, a new spill Teletype was sent, detailing the dates for BiOp (75kcfs) and 50kcfs spill.  The pre-test started on 17 June.  The testing period is from 20 June through 07 August.

  - Please see attached MEMORANDUM FOR THE RECORD dated 10 July 2004.

  - On 6 July, a new Teletype was sent indicating a restricted Forebay elevation not to exceed 72.0 MSL between 0700 and 1700 hours on 12 and 13 July to assist final work on the Drano Lake boat launch.

JAMES R. MAHAR, P.E.

Operations Manager

//S/