### CENWP-OP-B                                                                                                                                     23 August 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 34 of 2004, which covers the period from 15 through 21 August 2004.

- OPERATION SUMMARY

  - Daily river flow averaged 128.5 to 169.5 kcfs.  Daily project tailwater elevation averaged 10.2’ to 13.1’ msl.  Daily project forebay elevation averaged 74.8’ to 76.0’ msl.  Daily river temperature averaged 70 to 71°F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B Branch respectively, are part of the FPP spill pattern.  Spill averaged 84.9 to 103.4 kcfs.  Control room indications do not reflect actual flow through the main dam.  Corrective actions are being coordinated at this time.  See misc. 6.1

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 18 remains out of service for 4-year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F2 was out of service from 1309 until 1423 on 16 August for trash rack raking.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

FV3-7- closed for cleaning from 1034 until 1110 on 17 August.

FV3-9- closed for cleaning from 1034 until 1110 on 17 August.

FV4-3- closed for repairs from 0920 until 1521 on 16 August.

  - STS/VBS Inspections.    No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage. No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampled one day last week due to temperatures above 72ºF.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA FISH lamprey.  Lamprey tagging continues.

  - PSMFC SMF.  No salmonids were observed sliding over the separator bars this week.

  - Univ. of Idaho.   Sampled one day last week due to temperatures above 72ºF.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 15 through 21 August this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel | This is a normal condition. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | No acoustic sensor | Will repair during winter 04/05 |  |
| 8/15 | Weir 38 | Water elevations <1.3’ | Unknown |  |  |
| 8/16-19, 21 | A and B branches | Water elevations >1.0’ | Still in shad passage mode. | Request sent to electricians. |  |
| 8/16-19, 21 | Cascades Island UMT | Water elevations >1.0’ | Still in shad passage mode. | Request sent to electricians. |  |
| 8/16, 18 | Weirs 37/38 | Water elevations >1.0’ | Still in shad passage mode. | Request sent to electricians. |  |

  - Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Measurements for the AFF are taken in the exit ladder.  Temperatures are in Fahrenheit.

| ##### Date | Wash. Shore daily average | Bradford Is. daily average | ##### AFF exit daily maximum |
| --- | --- | --- | --- |
| 8/15 | 73.7 | 73.9 | 73.9 |
| 8/16 | 73.4 | 73.6 | 73.7 |
| 8/17 | 73.3 | 73.4 | 73.5 |
| 8/18 | 73.2 | 73.3 | 73.4 |
| 8/19 | 73.2 | 73.3 | 73.4 |
| 8/20 | 73.3 | 73.4 | 73.6 |
| 8/21 | 73.4 | 73.4 | 73.7 |

  - Sensor Calibration.  Calibration was checked on 19 August this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

  - PH 1 Gantry Crane Delivery and Erection.  Scheduled for 9 August through 4 December.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - On 09 August, the Project received the latest teletype for spill.  Increase each spill bay opening by 0.3 foot over the opening shown in the Fish Passage Plan during daytime and minimum spill periods to meet BiOp spill requirements.

  - DSM2 mechanical screen sweeps are exercised once a week.

JAMES R. MAHAR, P.E.

Operations Manager

//S/