### CENWP-OP-B                                                                                                                                  03 October 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 40 of 2004, which covers the period from 26 September through 02 October 2004.

- OPERATION SUMMARY

  - Daily river flow averaged 92.6 to 123.9 kcfs.  Daily project tailwater elevation averaged 9.0’ to 12.0’ msl.  Daily project forebay elevation averaged 75.4’ to 76.0’ msl.  Daily river temperature averaged 63°F.  Daily turbidity measured 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply adult attraction flow for Cascades Island and B Branch respectively, are open during daylight hours (0500 until 1930).  Spill averaged 2.1 to 2.3 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 2 was out of service from 0638 until 1527 on 30 September to facilitate Unit 1 testing.

    - Units 9 and 10 remain out of service for gantry crane three construction.

    - Unit 15 3D CAM remains in manual.  Unit 15 had a 1% violation from 0800 until 0830 on 27 September due to STS inspections.

    - Unit 16 had a 1% violation from 0830 until 0900 on 27 September.

    - Unit 18 remains out of service for 4-year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting week:

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 15 | 9/27 | 165 |  |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage. No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampling continues twice a week.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - PSMFC SMF.  Two salmon were observed sliding over the separator bars this week.

  - Univ. of Idaho.  Tagging concluded 01 October.

  - USGS.  Monitoring continues.

  - WDFW Fish Counting.  16-hr visual counts at Washington Shore and Bradford Island.

  - WDFW/ODFW.  Tule counting started on 15 August and will continue until 15 October.

- FISHWAYS

  - Project biologists inspected 26 through 30 September and FFU biologists inspected 01-02 October this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel | This is a normal condition. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | No acoustic sensor | Will repair during winter 04/05 |  |
| 9/27 | PH1 units | Unit 4 operated out of FPP priority. | Unit 3 was shutdown first. | Operators corrected unit operations. |  |
| 9/27 | Weir 37 | Reading <1.0’> |  | Operators blew down drain. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.   Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| ##### Date | Wash. Shore daily average | Bradford Is. daily average |
| --- | --- | --- |
| 9/26 | 65.7 | 65.7 |
| 9/27 | 65.6 | 65.6 |
| 9/28 | 65.7 | 65.7 |
| 9/29 | 65.7 | 65.6 |
| 9/30 | 65.4 | 65.4 |
| 10/01 | 65.0 | 65.1 |
| 10/02 | 64.7 | 64.7 |

Table 3.  Fishway Temperatures.

  - Sensor Calibration.  Calibration was checked on 29 September this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Current schedule is set for installation in WA ladder for Winter 04/05.

  - PH 1 Gantry Crane Delivery and Erection.  Construction will continue through 04 December.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island computer is not controlling properly.  The fishway is currently in manual operation and maintaining criteria.

  - Juvenile Fishways.

    - DSM1 continues to run south with STSs and VBSs in Units 2 and 3.

- HAZMAT, SPILLS AND CLEANUP

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - A teletype issued on 24 September requests a forebay hard constraint of 75.0’ – 76.5’ from 0600 on 27 September until 1800 on 30 September.  This is to reduce wear and tear on tribal gill net equipment.  A teletype issued on 01 October extends this operation from 04 through 08 October.

  - The winter maintenance schedule is available.  Please contact Fisheries.

  - To volunteer for the winter dewatering activities, please call Tammy Mackey at 541-374-4552.

JAMES R. MAHAR, P.E.

Operations Manager

//S/