### CENWP-OP-B                                                                                                                                  14 November 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 46 of 2004, which covers the period from 07 November through 13 November 2004.

- OPERATION SUMMARY

  - Daily average river flows ranged from 115.4 to 121.6 kcfs.  Daily average project tailwater elevation ranged from 10.8’ to 11.5’ msl.  Daily average project forebay elevation ranged from 74.0’ to 74.9’ msl.  Daily average river temperature ranged from 53 to 55F.  Daily turbidity measured 6.0 to 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply adult attraction flow for Cascades Island and B Branch respectively, are open during daylight hours (0500 until 1930).  Daily average spill ranged from 2.2 to 2.3 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 2 remains out of service for turbine rehab.

    - Units 7, 8, and 9 were out of service from 1040 until 1550 on 08 November to facilitate the delivery of the crane barge.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 18 returned to service at 0823 on 09 November.  Unit 18 was out of service from 1640 on 09 November until 0845 on 10 November due to governor trouble.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

    - FV 1-1- from 1530 until 1554 on 08 November.

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - WDFW Chum.  Chum trapping and tagging starts 04 November through 22 November.

  - WDFW Fish Counting.  Fish counting with video began on 01 November at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 07, 09-11, and 13 November.  FFU inspected on 12 November.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Meter in slowest part of the channel | This is a normal condition. |  |
| All week | PH2 PCC | Velocity < 1.5 fps | No acoustic sensor | Replace this winter |  |
| 11/08 | Bonneville | No inspection by fish bio | Scheduling conflicts |  |  |
| 11/07, 11/09, 11/13 | BI, A-Branch, B-Branch | Weir reading <1.0> | Low forebay elevations. | Operators corrected. |  |
| 11/11-13 | PH1 ITS | Chain gate 6C closed | Closed to facilitate crane barge delivery | Will correct Mon. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Fahrenheit.

| ##### Date | Wash. Shore daily avg. | Bradford Is. daily avg. |
| --- | --- | --- |
| 11/07 | 54.0 | 54.0 |
| 11/08 | 53.7 | 53.8 |
| 11/09 | 53.5 | 53.7 |
| 11/10 | 53.5 | 53.7 |
| 11/11 | 53.5 | 53.6 |
| 11/12 | 53.2 | 53.3 |
| 11/13 | 52.9 | 52.9 |

Table 3.  Fishway Temperatures.

  - Sensor Calibration.  Calibration was checked on 11 November this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction to start 29 November.

  - PH 1 Gantry Crane Delivery and Erection.  Construction will continue through 04 December.

  - North Monolith repairs.  Plans and specs not yet completed.

  - B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island remains in manual and maintaining criteria.

  - Juvenile Fishways.

    - DSM1 continues to run south with STSs and VBSs in Units 1 and 3.

    - The SMF is in bypass mode.  Mechanical screen sweeps were operated on 08 November.

- HAZMAT, SPILLS AND CLEANUP

Nothing to report this week.

- MISCELLANEOUS AND OTHER NOTEWORTHY ITEMS

  - A teletype issued on 09 November requests the following tailwater elevations to facilitate chum spawning  downstream of Bonneville Dam.  09 November- a tailwater hard constraint minimum of 10.5’ msl 24 hours a day and between 11.3’ to 11.7’ msl between 0700 until 1900.  10 November- a tailwater hard constraint minimum of 11.3’ msl 24 hours a day and between 11.3’ to 11.7’ msl between 0700 and 1900 daily.  This is to continue until further notice.

  - A teletype issued on 12 November requests the following tailwater elevations to facility a chum spawning study on 17-19 November.  The study requires ramping flows up and then down over a 10 hour period to determine how flow velocity affects chum behavior.

    - 17 November-

0500 hrs increase TW from 11.5’ to 12.7’

0700 hrs increase TW from 12.7’ to 13.9’

0900 hrs increase TW from 13.9’ to 15.1’

1100 hrs decrease TW from 15.1’ to 13.9’

1300 hrs decrease TW from 13.9’ to 12.7’

1500 hrs decrease TW from 12.7’ to 11.5’

    - 18 November through 19 November-

1600 hrs. increase TW from 11.5’ to 12.7’

1800 hrs. increase TW from 12.7’ to 13.9’

2000 hrs. increase TW from 13.9’ to 15.1’

2200 hrs. decrease TW from 15.1’ to 13.9’

2400 hrs. decrease TW from 13.9’ to 12.7’

0200 hrs. decrease TW from 12.7’ to 11.5’

JAMES R. MAHAR, P.E.

Operations Manager

//S/