### CENWP-OP-B                                                                                                                                  13 December 2004

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 51 of 2004, which covers the period from 12 through 18 December 2004.

- OPERATION SUMMARY

  - Daily average river flows ranged from 135.8 to 192.6 kcfs.  Daily average project tailwater elevation ranged from 14.0’ to 16.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.6’ to 75.0’ msl.  Daily average river temperature ranged from 46 to 48F.  Daily turbidity measured 5.0 to 7.0 on the secchi disk.

  - Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 1.0 to 1.8 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 1 was out of service from 0736 until 0741 on 12 December for governor testing and from 0735 until 0858 on 15 December for STS removal.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service from 1047 until 1205 on 15 December for STS removal.

    - Unit 8 was out of service from 0951 until 1112 and from 1121 until 1438 on 16 December due to governor problems.  Unit 8 operated outside the 1% curve from 1440 until 1635 on 18 December to facilitate trashrack raking.

    - Unit 9 operated outside the 1% curve from 1002 until 1420 on 18 December to facilitate trashrack raking.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service for unit overhaul.

    - Unit 12 was out of service from 1002 until 1116 on 17 December for STS removal.

    - Unit 13 was out of service from 1330 until 1345 on 15 December due to a T-11 outage and from 0630 until 0910 on 17 December for STS removal.

    - Unit 14 was out of service from 1330 until 1345 on 15 December due to a T-11 outage and from 0630 until 0910 on 17 December for STS removal.

    - Unit 15 was out of service from 1310 until 1520 on 16 December for STS removal.

    - Unit 16 was out of service from 1100 until 1310 on 16 December for STS removal.

    - Unit 17 was out of service from 1936 until 2303 on 16 December due to drawdowns exceeding 2.0’ and from 1122 until 1518 on 17 December for STS removal.

    - Unit 18 was out of service from 0907 until 1058 on 16 December for STS removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

    - Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.  Drawdowns exceeded 2.0’ at Unit 17 on 13 and 16 December.

- ACTIVITIES

  - AWS Closures.  The following AWS valves activity occurred this reporting week.

    - FV1-1- switched to manual at 0530 on 13 December due to excessive drawdown.  Closed for cleaning from 1300 until 1338 on 14 December.  Closed to float trash from 0300 until 0345 on 16 December, 0440 until 0515 on 17 December and 2110 on 18 December.

    - FV3-7- switched to manual from 0041 until 0516 on 13 December due to excessive drawdown.

    - FV3-9- switched to manual from 0041 until 0516 on 13 December due to excessive drawdown.  Closed for cleaning from 1245 until 1300 on 14 December.

    - FV 6-9- remains closed.

  - STS/VBS Inspections.  The following STSs/VBSs were removed this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1 | 12/15 |  | REMOVED UNTIL SEPTEMBER |
| 3 | 12/15 |  | REMOVED UNTIL SEPTEMBER |
| 11 | 11/15 |  | REMOVED FOR OVERHAUL |
| 12 | 12/17 |  | REMOVED FOR WINTER MAINTENANCE |
| 13 | 12/17 |  | REMOVED FOR WINTER MAINTENANCE |
| 14 | 12/17 |  | REMOVED FOR WINTER MAINTENANCE |
| 15 | 12/16 |  | REMOVED FOR WINTER MAINTENANCE |
| 16 | 12/16 |  | REMOVED FOR WINTER MAINTENANCE |
| 17 | 12/17 |  | REMOVED FOR WINTER MAINTENANCE |
| 18 | 12/16 |  | REMOVED FOR WINTER MAINTENANCE |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

    - South Monolith.  Biologists removed two juvenile chinook, four peamouth and three northern pikeminnow from the South Monolith at Washington Shore on 14 December.

    - DSM1.  Biologists removed three juvenile shad, one juvenile unclipped steelhead and one juvenile chinook from the DSM1 channel on 15 December.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

- FISHWAYS

  - Project biologists inspected 13, 15, and 17 December

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| 12/13 | BI fishway | Weirs reading < 1.0’ | Trashrack drawdown | Riggers cleaning the trashracks. |  |
| 12/13 | BI fishway | Trashrack drawdown | Debris | Riggers to clean |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  Calibration was checked on 17 December this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction continues.

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - North Monolith repairs.  Plans and specs not yet completed.

  - B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island fishway PLC remains in manual and maintaining criteria.   The exit is open.

    - Washington Shore fishway, AWS, and AFF remain dewatered.

  - Juvenile Fishways.

    - DSM 1 is dewatered.

    - DSM2 orifice lights were turned off on 18 December to encourage fish to move out before the channel is dewatered on 20 December.

  - UPCOMING ACTIVITIES

    - DSM2/Two mile pipe dewatering and fish salvage on 20/21 December.

- HAZMAT, SPILLS AND CLEANUP- Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype issued on 15 December requests a tailwater hard constraint minimum of 11.9’ during all hours; a tailwater hard constraint between 11.9’ and 12.3’ between the hours of 0700 to 1900 daily, with a target of 11.9’; and the highest tailwaters to occur between 1900- 0700 hours if required by flow condition.  This operation is to facilitate chum spawning around Ives and Pierce Islands.

  - A teletype issued on 16 December requests a special tailwater operation of 11.9’ to 12.3’ on 16 December only.

  - Teletypes issued on 17 and 18 December allows special operations to avoid overfilling the reservoir.

  - Embrace a Stream grant application for Bass Lake monitoring and public workshop to be submitted to Trout Unlimited by 20 December.

JAMES R. MAHAR, P.E.

Operations Manager

//S/