### CENWP-OP-B                                                                                                                                  18 January 2005

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 03 of 2005, which covers the period from 09 through 15 January 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 120.1 to 198.0 kcfs.  Daily average project tailwater elevation ranged from 12.4’ to 16.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.4’ msl.  Daily average river temperature remained 41F.  Daily turbidity measured 6.0 to 7.0 on the secchi disk.

  - Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 1.0 to 1.1 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 1 was out of service from 1325 until 1330 on 11 January due to low governor oil pressure.  Unit 1 also operated outside the 1% curve at 0810 on 13 January to facilitate testing.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service for unit overhaul.

    - Unit 14 was out of service from 0550 until 1306 on 10 January due to a tripped exciter.  Unit 14 also operated out of the 1% curve at 1350 to facilitate troubleshooting the exciter.

    - Unit 18 was out of service from 0416 on 10 January until 1526 on 13 January.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

    - Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves activity occurred this reporting week.

    - FV1-1- Closed for cleaning from 0803 until 0838 on 13 January.

    - FV3-7- Closed for cleaning from 1018 until 1102 on 13 January.

    - FV3-9- Closed for cleaning from 1556 until 1610 on 11 January and from 1102 until 1145 on 13 January.

    - FV 6-9- remains closed.

  - STS/VBS Inspections.  STSs/VBSs have been removed until February.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

- FISHWAYS

  - Project biologists inspected 10-14 January.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| 1/12, 1/14 | PH1 WG2 | Opening < 8’ | Unknown | Adjusted WG 2 | 05-10052 |
| 1/10-11, 1/13-14 | FG3-4 | Incorrect position for TW | Bent shaft | See Fishway Status 6.1.2 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  Calibration was checked on 13 January this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction continues.

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - North Monolith repairs.  Plans and specs not yet completed.

  - B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLC remains in manual and maintaining criteria.   The Cascades Island exit is open.

    - A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-5 has been set to FG3-4 criteria, FG3-6 to FG3-5 criteria, and so on.  FG3-4 will remain out of service until the winter maintenance period 2005/06.

    - Washington Shore fishway, AWS, and AFF remain dewatered.

  - Juvenile Fishways.

    - DSM 1 remains dewatered.

    - DSM2 remains dewatered.

  - Upcoming Events.

    - North monolith dewatering scheduled to start 18 January.

    - Two mile pipe survey tentatively scheduled mid to late January.

- HAZMAT, SPILLS AND CLEANUP- Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype issued on 07 January switches PH2 Unit 18 back to normal operating priority, first on and last off.

JAMES R. MAHAR, P.E.

Operations Manager

//S/