### CENWP-OP-B                                                                                                                                  31 January 2005

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 05 of 2005, which covers the period from 23 through 29 January 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 134.5 to 162.7 kcfs.  Daily average project tailwater elevation ranged from 12.8’ to 14.9’ msl.  Daily average powerhouse forebay elevation ranged from 74.7’ to 75.6’ msl.  Daily average river temperature averaged 39F.  Daily turbidity measured 7.0 on the secchi disk.

  - Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 1.0 to 1.1 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service for unit overhaul.

    - Unit 13 was out of service from 0641 until 1607 on 24 January due to oil in the gatewell.  See 7.1

    - Unit 17 was out of service from 0634 on 24 January until 0759 on 26 January for modifications for a new XJ annunciator.

    - Unit 18 was out of service from 1211 until 1337 on 26 January for exciter fan repairs.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

    - Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves activity occurred this reporting week.

    - FV1-1- Closed for cleaning from 1550 until 1627 on 28 January.

    - FV3-7- Closed for cleaning from 1007 until 1110 on 28 January.

    - FV3-9- Closed for cleaning from 1518 until 1523 on 25 January and from 1607 until 1637 on 27 January.

    - FV 6-9- remains closed.

  - STS/VBS Inspections.  STSs/VBSs have been removed until February.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

- FISHWAYS

  - Project biologists inspected 24-26, 28 January.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| 1/24, 1/26 | BI fishway | Entrance <1.0’ | Faulty elevation. Sensor. | System in manual |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  Calibration was checked on 26 January this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction continues.

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - North Monolith repairs.  Construction tentatively scheduled for February.

  - B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLC remains in manual and maintaining criteria.   The Cascades Island exit is open.

    - A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.

    - Washington Shore fishway, AWS, and AFF remain dewatered.

  - Juvenile Fishways.

    - DSM 1 remains dewatered.

    - DSM2 remains dewatered.

  - Upcoming Events.

    - Two mile pipe survey tentatively scheduled for early February.

- HAZMAT, SPILLS AND CLEANUP

  - On 23 January, oil was noticed dripping from the STS drive shaft at 13A.  The unit was not operating at the time.  Clean-up started on the 23rd and continued until WA DOE signed off on 25 January.  Final determinations of the amount of oil lost have not yet been completed.

- TELETYPES AND OTHER NOTEWORTHY ITEMS – Nothing to report this week.

JAMES R. MAHAR, P.E.

Operations Manager

//S/