### CENWP-OP-B                                                                                                                                  15 February 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 07 of 2005, which covers the period from 06 through 12 February 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 149.1 to 167.1 kcfs.  Daily average project tailwater elevation ranged from 14.1’ to 14.7’ msl.  Daily average powerhouse forebay elevation ranged from 74.7’ to 75.1’ msl.  Daily average river temperature averaged 40 to 41F.  Daily turbidity measured 7.0 on the secchi disk.

  - Spill Bay 1, which supplies adult attraction flow for Cascades Island, is open during daylight hours.   Daily average spill ranged from 0.9 to 1.1 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 7 operated outside the 1% curve from 1027 until 1205 and from 1351 until 1627 on 10 February to facilitate trashrack raking.

    - Unit 9 was out of service from 0705 until 0721 on 10 February due to a breaker trip.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 13 was out of service from 2250 on 10 February until 0707 on 11 February due to no PSS.

    - Unit 14 was out of service from 0700 on 07 February until 1200 on 10 February due to breaker mods.

    - Unit 16 was out of service from 1208 on 10 February until 1641 on 11 February due to breaker mods.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Fish Unit 1 remains out of service for winter maintenance at the Washington Shore fishway.

    - Fish Unit 2 remains out of service for winter maintenance at the Washington Shore fishway.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves activity occurred this reporting week.

    - FV1-1- Closed for cleaning from 1305 until 1318 on 07 February.

    - FV 6-9- remains closed.

  - STS/VBS Inspections.  STSs/VBSs for PH2 have been scheduled for installation the week of 21 February.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Univ of Idaho.  Installing and repairing antennas in the north monolith and Washington Shore fishway.  Installation of a half duplex PIT tag detector system is scheduled for mid to late February.

  - NOAA Fish.  Prototype lamprey flume to be installed 24 February.  Additional installation of above water equipment will occur in April.

  - USGS FPE and Survival.  Installing radio telemetry equipment.

  - WDFW Fish Counting.  Video counting continues at Bradford Island and Cascades Island.

- FISHWAYS

  - Project biologists inspected 07 through 11 February.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  Calibration was checked on 10 February this reporting week.  PH1 south and central collection channel sensors need to be recalibrated.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction continues.

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - North Monolith repairs.  Construction started.

  - B2 Follow on.  Mods to the perf plate and the bypass flume to be completed in February 2005.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLC remains in manual and maintaining criteria.   The Cascades Island exit is open.

    - A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.

    - Washington Shore fishway, AWS, and AFF remain dewatered.

  - Juvenile Fishways.

    - DSM 1 remains dewatered.

    - DSM2 remains dewatered.  Scheduled water up date is 21 February.

  - Upcoming Events.

    - ROV inspection of BI and Cascades Island scheduled for 22 February.

    - Installation of a guide wall, lamprey flume and half –duplex PIT tag detectors will occur on 24 February at the north monolith NDE.  Divers are expected to complete the work in one day.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS – Nothing to report this week.

JAMES R. MAHAR, P.E.

Operations Manager

//S/