### CENWP-OP-B                                                                                                                                  06 March 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 10 of 2005, which covers the period from 27 February through 05 March 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 119.5 to 142.7 kcfs.  Daily average project tailwater elevation ranged from 11.6’ to 13.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.4’ to 75.9’ msl.  Daily average river temperature averaged 41 to 42F.  Daily turbidity measured 7.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.   Daily average spill ranged from 0.0 to 1.4 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 18 was out of service from 1320 until 2136 on 03 March due to a loose north servo linkage pin.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Fish Unit 1 returned to service at 1118 on 01 March.

    - Fish Unit 2 returned to service at 1950 on 28 February.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed for cleaning this reporting week.

    - FV 1-1- from 1257 until 1315 on 02 March.

    - FV6-9 returned to service in manual on 28 February and to auto on 01 March.

  - STS/VBS Inspections.  The following STSs/VBSs were installed this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 15 | 2/28 |  |  |

Table 1.  STS Installation Dates.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Univ of Idaho.  All antennas installed/repaired.

  - NOAA Fish.  Prototype lamprey flume installed.  Installation of above water equipment will occur in April.

  - PSMFC.  Smolt monitoring was initiated on 01 March.  See section 6.2.3

  - Spring Creek NFH.  Release of tule chinook occurred on 02 March.

  - USGS FPE and Survival.  Installing radio telemetry equipment.

  - Battelle FPE and FGE.  Installing hydroacoustic transducers.

  - WDFW Fish Counting.  Video counting continues at Bradford Island, Cascades Island, and Washington Shore.

- FISHWAYS

  - Project biologists inspected 27 February – 05 March.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| 3/1, 3/3-3/5 | PH2 SCCH | Velocity <1.5 fps | Unknown |  |  |
| 3/1-3/5 | SMF hydrocannons | Out of service | Faulty pipe and fittings | New parts are on order. |  |
| 3/4 | B-branch TW/ Ent diff. | Too low | Unknown | Control put in manual |  |
| 3/5 | CI fishway | FG6-12 stuck closed | Bent shaft. | FG6-11 will be used to compensate. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 3/1 | 41.2 | 41.4 |
| 3/2 | 41.4 | 41.7 |
| 3/3 | 41.5 | 41.8 |
| 3/4 | 41.6 | 41.8 |
| 3/5 | 41.7 | 42.0 |

  - Sensor Calibration.  Calibration was checked on 04 March.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - Adult PIT tag exit detectors.  Washington Shore construction completed on 28 February.

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in Winter 05/06.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLC returned to auto on 01 March.  BI stopped controlling properly on 05 March and is back in manual.  The Cascades Island exit remains open.

    - A-branch diffusers have been reprogrammed to compensate for FG3-4 being out of service.  FG3-4 will remain out of service until the winter maintenance period 2005/06.

    - Washington Shore fishway, and AWS returned to service at 1100 on 28 February.

    - The AFF remains dewatered.

  - Juvenile Fishways.

    - DSM 1 remains dewatered.

    - SMF hydrocannons are out of service due to shrinkage in the PVC pipes.  New parts are on order.  The booster pump is on order.

    - The SMF switch gate was moved from “Bypass” to “Sample” from 0630 until 1600 on 01 March, from 0645 until 1600 on 02 March, and at 0645 on 03 March and remains in “Sample”.

  - Upcoming Events.

    - Spring Creek released tule chinook on 02 March.

    - B2CC was open from 1540 on 03 March until 1530 on 05 March to facilitate the Spring Creek release.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 02 March requests operation of the second powerhouse corner collector beginning 03 March.  When the corner collector is operating, maintain a minimum tailwater elevation of 12.5 feet and keep spill bays 1 and 18 closed.

  - A teletype issued on 04 March requests that the second powerhouse corner collector be closed at 1700 hours on 05 March and that spill bays 1 and 18 return to normal operation as stated in the FPP, effective 06 March when daytime spill begins.

  - Marine mammals have been observed in the tailraces of PH1, PH2 and the Main Dam as well as the forebay.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.

JAMES R. MAHAR, P.E.

Operations Manager

//S/