### CENWP-OP-B                                                                                                                                  03 April 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 14 of 2005, which covers the period from 27 March through 02 April 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 111.8 to 170.6 kcfs.  Daily average project tailwater elevation ranged from 11.9’ to 15.5’ msl.  Daily average powerhouse forebay elevation ranged from 75.2’ to 76.0’ msl.  Daily average river temperature averaged 46F.  Daily turbidity measured 4.0 to 6.0 on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.   Daily average spill ranged from 1.3 to 1.5 kcfs.

  - Unit operation.

    - Unit 0 remains out of service for a 5-year overhaul.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 was out of service from 0650 until 1128 on 28 March for transducer installation.

    - Unit 12 was out of service from 1134 until 1440 on 28 March for transducer installation.

    - Unit 13 was out of service from 0648 until 1027 on 29 March for transducer installation.

    - Unit 14 was out of service from 1030 until 1320 on 29 March for transducer installation.

    - Unit 15 was out of service from 1325 until 1605 on 29 March for transducer installation.

    - Unit 16 was out of service from 0720 until 0807 on 30 March for transducer installation.

    - Unit 17 was out of service from 0815 until 0848 on 30 March for transducer installation.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting week.

  - STS/VBS Inspections.   The following STSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 3/28 | 813 |  |
| 12 | 3/28 | 711 |  |
| 13 | 3/29 | 677 |  |
| 14 | 3/29 | 667 |  |
| 15 | 3/29 | 662 |  |
| 16 | 3/30 | 747 |  |
| 17 | 3/30 | 780 |  |
| 18 | 3/30 | 769 |  |

Table 1.  STS Inspections.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Univ of Idaho.  Nothing new to report.

  - NOAA Fish.  Nothing new to report.

  - PSMFC.  One steelhead kelt was removed from the separator bars and released alive.   Seventy-seven adult steelhead were observed crossing the separator bars this week.

  - USGS FPE and Survival.  Installing radio telemetry equipment.

  - Battelle FPE and FGE.  Installing hydroacoustic transducers.

  - WDFW Fish Counting.  16-hr visual counts began 01 April at Washington Shore and Bradford Island.

  - USDA Wildlife Services.   Hazing activities of gulls commenced this week.

- FISHWAYS

  - Project biologists inspected 27 March through 02 April.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | No action taken until S. monolith can be dewatered. |  |
| 3/28, 3/29 | B-Branch | Entrance diff. < 1.0 | Sensors not functioning properly | Operators corrected |  |
| 3/31 | NDE | Gate < 13’ | Unknown |  |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 3/27 | 46.1 | 46.3 |
| 3/28 | 46.3 | 46.4 |
| 3/29 | 46.3 | 46.3 |
| 3/30 | 46.1 | 46.3 |
| 3/31 | 46.4 | 46.6 |
| 4/1 | 46.4 | 46.7 |
| 4/2 | 46.5 | 46.7 |

  - Sensor Calibration.  Calibration was checked on 02 April.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - PH 1 Gantry Crane Delivery and Erection.  Construction continues.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in Winter 05/06.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLCs are in manual.

    - Cascades Island diffuser FG6-11 will be used to compensate for FG6-12’s bent shaft.  FG6-12 will remain out of service until winter 2006/07.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

    - The AFF will be watered up on 05 April.

  - Juvenile Fishways.

    - SMF booster pump is on order.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - Marine mammals have been observed in the tailrace, the forebay, and the fishways.  The project is not taking action to harass, harm, or otherwise annoy these animals.

JAMES R. MAHAR, P.E.

Operations Manager

//S/