### CENWP-OP-B                                                                                                                                  08 May 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 19 of 2005, which covers the period from 01 through 07 May 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 167.7 to 202.5 kcfs.  Daily average project tailwater elevation ranged from 14.8’ to 17.3’ msl.  Daily average powerhouse forebay elevation ranged from 74.8’ to 75.8’ msl.  Daily average river temperature ranged from 53 to 56F.  Secchi disk measurements ranged from 4.0 to 6.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 64.9 to 80.1 kcfs.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 9 returned to service at 1535 on 02 May.

    - Unit 10 remains out of service for gantry crane three construction.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV5-4 closed for cleaning from 0744 until 0920 on 05 May.

  - STS/VBS Inspections.   No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle FPE and FGE.  DIDSON barge installed at PH1 on 04 May.

  - CRITFC.  Sampling continues twice a week through the summer.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Fisheries Field Unit.  Monitoring and hazing of marine mammals entering the fishways.  See. 8.1

  - NOAA barge transportation study.  Barge arrival dates are tentatively scheduled for 30 April, 4, 14, and 20 May between 1930 and 0200 hours.  Tagged fish releases will occur 48 hours later.

  - ODFW Pikeminnow Tagging.  Electrofishing in Bonneville’s forebay and tailrace will continue 9-13 May.

  - PSMFC.   Observed fallbacks included 13 steelhead, two salmon and one unknown salmonid.  Research fish collected included; 325 clipped yearling chinook and 50 coho for NMFS; 540 clipped yearling chinook and 150 clipped steelhead for USGS.

  - Spring Creek NFH.  Released approximately 340,000 tule fall chinook on 12 May.

  - Univ of Idaho.  UI researchers are assisting with the marine mammal hazing.   Trapping continues.

  - USDA Wildlife Services.   Hazing activities for gulls and sea lions continue.

  - USGS FPE and Survival.  Installation of radio telemetry equipment complete.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 01 through 07 May.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | No action taken until winter maintenance. |  |
| All week | Cascades Island | FG6-12 OOS | Bent shaft | FG6-11 to compensate see 6.1.2 |  |
| 5/5 | Cascades Island | FV5-4 closed, differential low | FV5-4 closed for cleaning | Back in criteria by 0930 |  |
| 5/7 | PH1 PCC | FV1-1 in manual, low differential | FV1-1 not operating correctly. | Operators submitted a TR. | #05-25093 |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/01 | 53.6 | 53.7 |
| 5/02 | 54.1 | 54.3 |
| 5/03 | 54.8 | 55.0 |
| 5/04 | 55.7 | 55.8 |
| 5/05 | 56.0 | 56.0 |
| 5/06 | 56.0 | 56.0 |
| 5/07 | 56.1 | 56.2 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 05 May.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - PH 1 Gantry Crane Delivery and Erection.  Crane testing performed this reporting week.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLCs are in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

  - Juvenile Fishways.

    - SMF booster pump installation continues this week.

    - PH1 ITS was closed from 0800 until 1030 on 04 May to facilitate the DIDSON barge installation.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - Marine mammals have been observed in the tailrace, forebay, and fishways.   FFU and UI are undertaking hazing activities; hydrophones are in the Washington Shore fishway entrance; sea lion exclusion devices are being designed for the fishway entrances.

  - Sea lion hazing activities were conducted on 05-06 May.  These activities included releasing M-80 type seal “bombs” from boats within the BRZ.

  - According to a 06 May teletype, tailwater constraints for chum incubation have ended.

JAMES R. MAHAR, P.E.

Operations Manager

//S/