### CENWP-OP-B                                                                                                                                  29 May 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 22 of 2005, which covers the period from 22 through 28 May 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 248.0 to 267.2 kcfs.  Daily average project tailwater elevation ranged from 19.8’ to 21.5’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 74.1’ msl.  Daily average river temperature ranged from 58 to 59F.  Secchi disk measurements ranged from 3.5 to 5.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 85.2 to 105.6 kcfs.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 9 was out of service from 0427 until 1536 on 24 May for Unit 2 loop test.

    - Unit 10 remains out of service for gantry crane three construction.

    - Units 11-18 had 1% violations on 24 May due to STS inspections.

    - Unit 12 was out of service from 1410 until 1606 on 25 May for STS repair.

    - Unit 13 was out of service from 1102 until 1405 on 25 May for STS repair.

    - Unit 14 was out of service from 0710 until 1110 on 23 May for transducer repair.  Out of service from 0732 until 1057 on 25 May for STS repair.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV1-1 closed for cleaning from 1033 until 1051 on 28 May.

    - FV3-7 closed for cleaning from 1500 until 1600 on 26 May.

    - FV3-9 closed for cleaning from 1350 until 1500 on 26 May and 1100 until 1112 on 28 May.

    - FV5-9 closed for cleaning from 1008 until 1016 on 28 May.

  - STS/VBS Inspections.   The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 5/24 | 687 |  |
| 12 | 5/24 | 684 | Small rip repaired on 5/25 |
| 13 | 5/24 | 587 | 1’ tears and missing rivets repaired on 5/25 |
| 14 | 5/24 | 586 | Large rip and missing rivets repaired on 5/25 |
| 15 | 5/24 | 656 |  |
| 16 | 5/24 | 439 |  |
| 17 | 5/24 | 653 |  |
| 18 | 5/24 | 695 |  |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle FPE and FGE.  The DIDSON camera is scheduled for installation on 18 and 19 May at PH1.

  - CRITFC.  Sampling continues twice a week through the summer.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Fisheries Field Unit (FFU).  Monitoring of marine mammals entering the fishways.  See. 8.1

  - NOAA barge transportation study.  Barge sampling complete.

  - NOAA Fish Lamprey.  The Bradford Island lamprey ramp went into operation on 25 May.

  - PSMFC.   Observed fallbacks: Nine steelhead, one salmon.  Fish for research included: 335 clipped yearling chinook and 25 coho for NMFS, 535 clipped yearling chinook and 530 clipped steelhead for USGS

  - Univ of Idaho.  Assisting with the marine mammal monitoring and observing.   Trapping in the AFF.

  - USDA Wildlife Services.   Hazing activities for gulls and sea lions continue.

  - USGS FPE and Survival.  Juvenile tracking continues.

  - USGS.  Assisting with marine mammal monitoring and observing.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 22 through 28 May.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | No action taken until winter maintenance. |  |
| All week | Cascades Is. | FG6-12 OOS | Bent shaft | See 6.1.2 |  |
| 5/22, 5/24 | Cascades Is. | UMT reading <1.3’ | Not in shad passage | TR submitted | #05-25786 |
| 5/22 | PH1 PCC | Diff <1.5’ | NCCH sensor not working, FV1-1 not properly controlling. | Operators took manual control of the collection channel. See 6.1.4 |  |
| 5/23 | Cascades Is. | Entrance differential > 2.0 | In manual | Operators adjusted |  |
| 5/23 | PH1 NCCH | Entrance differential > 2.0 | In manual | Operators adjusted |  |
| 5/24 | Bradford Is. weir | Reading <1.2’ | Stillwell plugged | Riggers cleaned stillwell on 25 May. |  |
| 5/25 | North monolith | NUE and NDE closed. | Bulkhead installation for SLEDS | See 6.1.5 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/22 | 57.6 | 57.7 |
| 5/23 | 57.7 | 57.8 |
| 5/24 | 57.8 | 57.9 |
| 5/25 | 57.9 | 58.1 |
| 5/26 | 58.3 | 58.4 |
| 5/27 | 58.8 | 58.9 |
| 5/28 | 59.3 | 59.4 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 27 May.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - PH 1 Gantry Crane Delivery and Erection.  Crane testing continues this reporting week.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be removed in August.

  - SMF Full flow PIT Tag Detectors.  CH2M Hill has been contracted to write the letter report.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island fishway PLCs are in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

    - On 23 May PCC transducer calibrations were completed and FV1-1 returned to auto.  NCCH sensor still OOS.  Channel elevation is now controlled from the center transducer (CCCH).

    - PH2 NUE gate raised from 1145 until 1230 on 23 May and NDE gate raised from 1015 until 1038 on 25 May for installation test of new sea lion exclusion gates (SLEDs).

  - Juvenile Fishways.

    - SMF remains in the high outfall.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - Marine mammals have been observed in the tailrace, forebay, and fishways.   FFU, UI, and USGS continue monitoring.  Hydrophones are in the Washington Shore fishway entrance and sea lion exclusion devices are being built for the fishway entrances.

  - A teletype issued on 26 May revises the 120% gas cap to 125 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/