### CENWP-OP-B                                                                                                                                  18 July 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 29 of 2005, which covers the period from 10 through 16 July 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 174.6 to 209.8 kcfs.  Daily average project tailwater elevation ranged from 15.2’ to 17.5’ msl.  Daily average powerhouse forebay elevation ranged from 75.0’ to 76.0’ msl.  Daily average river temperature ranged from 67 to 69F.  Secchi disk measurements ranged from 5.0 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 88.4 to 97.1 kcfs.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 1 was out of service from 0339 until 2008 on 12 July for 90-deck crane rail bus work.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service from 0306 until 2053 on 12 July for 90-deck crane rail bus work.

    - Unit 4 was out of service from 0306 until 2053 on 12 July for 90-deck crane rail bus work.

    - Unit 5 was out of service from 0311 on 11 July until 1720 on 14 July for annual maintenance and bank 5/6 biannual maintenance.

    - Unit 6 was out of service from 0311 on 11 July until 1720 on 14 July for bank 5/6 biannual maintenance.

    - Unit 7 was out of service from 0307 until 2052 on 12 July for 90-deck crane rail bus work.

    - Unit 8 was out of service from 0307 until 2052 on 12 July for 90-deck crane rail bus work.

    - Unit 9 was out of service from 0325 until 2028 on 12 July for 90-deck crane rail bus work.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 16 was out of service at 2255 on 08 July until 1612 on 14 July for governor control work.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F1 was out of service form 0540 until 1257 on 11 July due to governor lock up.  Out of service from 1706 on 11 July until 1152 on 12 July due to loss of governor control.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV3-9 closed for cleaning from 0730 until 0740 on 12 July.

  - STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle FPE and FGE.  Monitoring continues.

  - CRITFC.  Sampling continues twice a week through the summer.

  - CTUIR.  Received 259 lamprey to date from NOAA Fisheries.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.   The NDE ramp installation is currently on hold.

  - PSMFC.   One fallback salmon was observed crossing the separator bars this week.  Subyearling chinook research fish collection: 1020 for USGS and 287 for NMFS.

  - Univ of Idaho.  Salmon trapping concluded until 01 August.  Lamprey trapping and testing continues.

  - USDA Wildlife Services.   Hazing activities for gulls continue.

  - USGS FPE and Survival.  Juvenile tracking continues.

  - Warm Springs Tribes.  Received 49 lamprey to date from NOAA Fisheries.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 10 July through 16 July.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Repairs scheduled for 06/07 |  |
| All week | B-Branch | North entrance gate closed. | Separated from shaft | See 6.1.6 |  |
| 7/11-12, 7/14-16 | Cascades Is. | FG6-12 OOS | Bent shaft | See 6.1.2 |  |
| 7/16 | DSM2 13B-S | Inoperable | Bolt damage on shaft | Operators submitted TR |  |
| 7/11-12 | PH2 PCC | F1 OOS | Governor trouble | See 6.1.5 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.   The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 7/10 | 67.1 | 67.0 | 67.2 |
| 7/11 | 67.6 | 67.4 | 67.6 |
| 7/12 | 68.4 | 68.3 | 68.5 |
| 7/13 | 68.7 | 68.5 | 68.7 |
| 7/14 | 68.6 | 68.8 | 68.7 |
| 7/15 | 68.9 | 68.9 | 68.9 |
| 7/16 | 69.0 | 69.1 | 69.1 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 14 July.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - PH 1 Gantry Crane Delivery and Erection.  Nothing new to report.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped in August.

  - SMF Full flow PIT Tag Detectors.  Possible exploratory drilling in the two mile pipe to look at hydraulics.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in auto.

    - Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

    - SLEDS remain in the out position until further notice due to structural damage.

    - PH2 collection channel configured for one fish unit operation from 0630 until 1329 on 11 July and from 1730 on 11 July until 1330 on 12 July.

    - B-Branch south entrance gate was opened on 14 July to compensate for the north entrance gate.

    - FV1-1 was put in manual on 16 July to maintain differential because the north and center collection channel sensors are out of service.

  - Juvenile Fishways.

    - DSM2 screen sweeps exercised at 1045 on 10 July.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype was issued on 13 July requesting that Bonneville pool be operated between elevation 74.5’ – 76.0’ for treaty gillnet fishing effective 0600 hrs Monday, 18 Jul 2005 - 1800 hrs Thurs, 21 Jul 2005.

  - A new teletype was issued on 11 July raising the gas cap to 155 kcfs.

JAMES R. MAHAR, P.E.

Operations Manager

//S/