### CENWP-OP-B                                                                                                                                  31 July 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 31 of 2005, which covers the period from 24 through 30 July 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 146.9 to 178.2 kcfs.  Daily average project tailwater elevation ranged from 13.7’ to 15.4’ msl.  Daily average powerhouse forebay elevation ranged from 75.0’ to 76.0’ msl.  Daily average river temperature ranged from 70 to 72F.  Secchi disk measurements ranged from 5.0 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 84.6 to 92.1 kcfs.

  - Unit operation.   PH1 operated out of FPP priority.  See 6.2.2

    - Unit 0 remains out of service due to governor trouble.

    - Unit 1 was out of service from 0800 until 1645 on 25 July for slip ring meggaring.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 4 remains out of service for a five-year overhaul and turbine obstruction removal.

    - Unit 5 was out of service from 1413 until 1518 on 27 July due to exciter trouble.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 had a 1% violation from 1525 until 1600 on 27 July due to STS inspections.

    - Unit 12 had a 1% violation from 1600 until 1625 on 27 July and on 28 July due to STS inspections.

    - Unit 13 returned to service at 1428 on 29 July and was out of service from 1518 until 1735 on 29 July due to a loss of power to the governor.

    - Unit 15 was out of service from 1823 on 26 July until 1456 on 28 July due to a T12 outage.

    - Unit 16 was out of service from 1506 until 1750 on 26 July due to URX relay trouble.  Unit 16 was out of service from 1823 on 26 July until 1445 on 28 July due to a T12 outage.

    - Unit 17 was out of service from 1823 on 26 July until 1508 on 28 July due to a T12 outage.

    - Unit 18 was out of service from 1823 on 26 July until 1445 on 28 July due to a T12 outage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F2 was out of service from 1823 on 26 July until 0311 on 27 July due to a T12 outage.  F2 was at standby from 1333 until 1356 on 28 July for switching.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV1-1- closed for cleaning from 1322 until 1348 on 25 July.

    - FV3-9- closed for cleaning from 1457 until 1515 on 28 July.

  - STS/VBS Inspections.   The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 7/27 | 742 |  |
| 12 | 7/28 | 569 |  |
| 13 | 7/25 | 255 |  |
| 14 | 7/25 | 410 |  |
| 15 | 7/25 | 562 |  |
| 16 | 7/25 | 636 |  |
| 17 | 7/25 | 416 |  |
| 18 | 7/25 | 701 |  |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle FPE and FGE.  Monitoring continues.

  - CRITFC.  Sampling for chinook is on hold until water temperatures drop below 70.0F.  See 6.1.5

  - CTUIR.  Received 259 lamprey to date from NOAA Fisheries.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.   Trapping and monitoring of the LPS continues.

  - PSMFC.   No kelts or fallback salmon was observed crossing the separator bars this week.

  - Univ of Idaho.  Trapping and tagging on hold until water temperatures drop.  See 6.1.5

  - USDA Wildlife Services.   Hazing activities for gulls continue.

  - USGS FPE and Survival.  Juvenile tracking continues.

  - Warm Springs Tribes.  Received 49 lamprey to date from NOAA Fisheries.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 24 July through 30 July.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Repairs scheduled for 06/07 |  |
| All week | B-Branch entrance | North entrance gate closed. | Separated from shaft | South gate open to compensate. See 6.1.4 |  |
| 7/24, 7/30 | Weir 38 | Reading <1.3> | Unknown | Valve #2 opened more. |  |
| 7/25 | A-Branch weir | Reading <1.3> | Unknown | No action taken |  |
| 7/26-29 | PH 1 Units | Operated out of FPP priority | Unit 2 testing |  |  |
| 7/27-30 | Cascades Is. | FG6-12 OOS | Bent shaft | See 6.1.2 |  |
| 7/27 | B-Branch entrance | Differential >2.0 | PLC in manual | Operators adjusted. |  |
| 7/27, 7/30 | B-Branch entrance | South gate closed. |  | Operators opened. |  |
| 7/30 | UMT weir | Reading <1.3> | FV5-9 adjusting. | No action taken |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.   The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 7/24 | 70.5 | 70.5 | 70.5 |
| 7/25 | 70.3 | 70.3 | 70.4 |
| 7/26 | 70.6 | 70.6 | 70.7 |
| 7/27 | 71.2 | 71.1 | 71.2 |
| 7/28 | 71.6 | 71.6 | 71.7 |
| 7/29 | 71.7 | 71.7 | 71.8 |
| 7/30 | 72.0 | 72.1 | 72.1 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 29 July.  All, except the B-Branch tailwater, sensors are within criteria.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications are scheduled to begin in winter 05/06.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - PH 1 Gantry Crane Delivery and Erection.  Nothing new to report.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped in August.

  - SMF Full flow PIT Tag Detectors.  Team meeting held on 28 July.  Hydraulic conditions at Location 1 discussed.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC back in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

    - B-Branch south entrance gate remains open to compensate for the north entrance gate.  Mechanics are waiting for a tailwater of 13’ or less before making repairs.

    - The AFF is closed to trapping until temperatures drop to 71.5F or until CRITFC receives the paperwork for mandatory steelhead sampling.

  - Juvenile Fishways.

    - Gatewell 13B was dewatered on 25 July to accommodate headgate HSS inspections.

    - PH1 units were operated out of FPP priority from 26-29 July to accommodate Unit 2 testing.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 22 July requests Bonneville pool be operated at a hard constraint of 75.0’ – 76.5’ and a soft constraint of 75.5’- 76.5’ for treaty gillnet fishing.  This forebay elevation is effective from 0600 on 25 Jul 2005 until 1800 on 29 Jul 2005.

JAMES R. MAHAR, P.E.

Operations Manager

//S/