### CENWP-OP-B                                                                                                                                  21August 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 34 of 2005, which covers the period from 14 through 20 August 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 123.8 to 154.2 kcfs.  Daily average project tailwater elevation ranged from 11.2’ to 13.8’ msl.  Daily average powerhouse forebay elevation ranged from 73.8’ to 75.6’ msl.  Daily average river temperature ranged from 71 to 72F.  Secchi disk measurements ranged from 6.0 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 75.2 to 87.8 kcfs.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 1 was operated out of FPP criteria from 17-18 August to facilitate precise alignment measurements for Unit 2 rehab work.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was operated out of FPP criteria from 17-18 August to facilitate precise alignment measurements for Unit 2 rehab work.

    - Unit 4 remains out of service for a five-year overhaul and turbine obstruction removal.

    - Unit 6 was operated out of FPP criteria from 17-18 August to facilitate precise alignment measurements for Unit 2 rehab work.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 15 went out of service at 0015 on 15 August for main unit circuit breaker replacement and annual maintenance.

    - Unit 16 went out of service at 0015 on 15 August for main unit circuit breaker replacement and annual maintenance.

    - Unit 17 went out of service at 0300 on 15 August to facilitate main unit circuit breaker replacement on Unit 16.  Unit 17 remained out of service until 1038 on 19 August due to a T12 outage.

    - Unit 18 went out of service at 0300 on 15 August to facilitate main unit circuit breaker replacement on Unit 16.  Unit 18 remained out of service until 1034 on 19 August due to a T12 outage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - Trashracks raked at F2 from 1148 until 1218 on 19 August.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting week

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

    - On 19 August, biologists removed one live sturgeon (20”) and three sculpin from Unit 4 tail logs.

- RESEARCH

  - CRITFC.  Chinook sampling voluntarily suspended until water temperatures drop below 70.0F.  No mandatory steelhead sampling at this time.

  - CTUIR.  Received 259 lamprey to date from NOAA Fisheries.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.  Washington Shore ramp started trapping on 18 August.  BI ramp continues to operate.

  - PSMFC.   No fallback or kelts were observed crossing the separator bars this week.

  - Univ of Idaho.  Trapping and tagging suspended until water temperatures drop.  See 6.1.5

  - Warm Springs Tribes.  Received 49 lamprey to date from NOAA Fisheries.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

  - WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island began on 15 August.

- FISHWAYS

  - Project biologists inspected 14 through 20 August.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Repairs scheduled for 06/07 |  |
| All week | B-Branch entrance | North entrance gate closed. | Separated from shaft | South gate open. See 6.1.4 |  |
| 8/14 | Bradford Is. | FG3-26 not in correct position. | System in manual. | Operators corrected |  |
| 8/14-15 | Weir 38 | Reading <1.3> | Unknown | No action taken |  |
| 8/15, 17 | DSM2 | 14B-S not in correct position. | Unknown |  |  |
| 8/16-17 | Weir 37 | Reading <1.0> | Still in shad mode. | TR submitted | #05-34694 |
| 8/16-17 | Bradford Is. weir | Reading <1.0> | Still in shad mode. | TR submitted | #05-34695 |
| 8/16-17 | A and B branch staff gauges. | Reading <1.0> | Still in shad mode. | TR submitted | #05-34695 |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 8/14 | 71.9 | 71.7 | 72.1 |
| 8/15 | 72.5 | 72.3 | 72.6 |
| 8/16 | 72.4 | 72.3 | 72.5 |
| 8/17 | 71.8 | 71.8 | 71.9 |
| 8/18 | 71.9 | 71.8 | 72.0 |
| 8/19 | 72.2 | 72.2 | 72.2 |
| 8/20 | 71.9 | 72.1 | 72.0 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 20 August.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods to start on 15 August with Units 15/16.

  - PH 1 Gantry Crane Delivery and Erection.  No new updates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped in August.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC went back to manual on 19 August.

    - Cascades Island diffuser FG6-12 has a bent shaft and will remain out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 will remain out of service until winter 2005/06.

    - B-Branch south entrance gate remains open to compensate for the north entrance gate.  Mechanics are waiting for a tailwater of 10’ or less before making repairs.

    - The AFF is closed to salmonid trapping until temperatures drop to 71.5F (as per the FPP) or until CRITFC receives the paperwork for mandatory steelhead sampling.

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

  - Upcoming Events.

    - The B2CC is scheduled for closure on 31 August.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A new teletype was issued on 02 August lowering the gas cap to 130 kcfs.

  - A new teletype was issued on 19 August requesting Bonneville pool to be operated at elevation 74.5-76.0 feet from 0600 hrs Monday, 22 Aug - 1800 hrs Friday, 26 Aug to limit wear and tear on gillnet equipment

  - The 2005/06 winter maintenance schedule will be available, in DRAFT form, by the September FPOM.

JAMES R. MAHAR, P.E.

Operations Manager

//S/