### CENWP-OP-B                                                                                                                                  28August 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 35 of 2005, which covers the period from 21 through 27 August 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 116.8 to 141.2 kcfs.  Daily average project tailwater elevation ranged from 10.8’ to 12.8’ msl.  Daily average powerhouse forebay elevation ranged from 75.3’ to 75.8’ msl.  Daily average river temperature ranged from 71 to 72F.  Secchi disk measurements ranged from 5.6 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 74.9 to 88.2 kcfs.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 4 returned to service at 1711 on 25 August.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 15 remains out of service for main unit circuit breaker replacement and annual maintenance.

    - Unit 16 remains out of service for main unit circuit breaker replacement and annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV1-1- closed for cleaning from 1618 until 1645 on 25 August.

    - FV3-9- closed for cleaning from 1618 until 1645 on 25 August.

    - FV5-9- closed for cleaning from 1618 until 1645 on 25 August.

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Chinook sampling voluntarily suspended until water temperatures drop below 70.0F.  Mandatory steelhead sampling began on 26 August.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.  Washington Shore and BI ramp continue to operate.

  - PSMFC.  No fallback or kelts were observed crossing the separator bars this week.

  - Univ of Idaho.  Trapping allowed four days/week.  See 6.1.5

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

  - WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island continues.

- FISHWAYS

  - Project biologists inspected 21 through 27 August.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | B-Branch | North gate closed. | Separated from shaft | See 6.1.4 |  |
| 8/25-27 | Spill bay 16 | Dogged at 3.0’ | Lifting beam out of alignment. | See 6.2.2 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 8/21 | 72.0 | 71.9 | 72.1 |
| 8/22 | 71.8 | 71.7 | 71.8 |
| 8/23 | 71.1 | 71.0 | 71.2 |
| 8/24 | 71.0 | 70.8 | 71.0 |
| 8/25 | 70.8 | 70.7 | 70.9 |
| 8/26 | 70.9 | 70.7 | 71.0 |
| 8/27 | 71.1 | 70.9 | 71.2 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 25 August.  Two PH1 PCC sensors are scheduled for replacement on 12-13 September.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods started on 15 August with Units 15/16.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.

    - B-Branch south entrance gate remains open to compensate for the north entrance gate.

    - The AFF is open for salmonid trapping four days a week, from 0600 until 1000, until temperatures drop to 69.5F (as per the FPP).

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

    - Due to concerns about safety, Bay 16 has been dogged off at two dogs (3.0’) until spill ends on 31 August.  The lifting beam is out of alignment with the gate.  The rest of the spillway remains in auto and will compensate for the extra .5’ of flow through Bay 16.

  - Upcoming Events.

    - The B2CC is scheduled for closure at 0900 on 31 August.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A 26 August teletype requests Bonneville to maintain a forebay of 75.0-76.5’ msl from 0600 on 29 August until 1800 on 31 August.  This is to limit wear and tear on tribal gillnet equipment.

  - The 2005/06 winter maintenance schedule will be available, in DRAFT form, by the September FPOM mtg.

JAMES R. MAHAR, P.E.

Operations Manager

//S/