### CENWP-OP-B                                                                                                                                  04 September 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 36 of 2005, which covers the period from 28 August through 03 September 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 97.3 to 138.8 kcfs.  Daily average project tailwater elevation ranged from 9.5’ to 12.2’ msl.  Daily average powerhouse forebay elevation ranged from 76.0’ to 76.3’ msl.  Daily average river temperature ranged from 70 to 71F.  Secchi disk measurements averaged 7.0 feet.

  - Daily average spill ranged from 1.5 to 82.2 kcfs.   Spill bay 16 was closed at 1510 on 31 August (see 8.2).   Spill season concluded at 0001 on 01 September.  Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours as of 01 September.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service from 0822 on 29 August until 1415 on 30 August due to transformer failure.

    - Unit 4 was out of service from 0822 on 29 August until 1415 on 30 August due to transformer failure.

    - Unit 5 had a 1% violation on 02 September during a load change.

    - Unit 6 went out of service at 0737 on 29 August for five-year overhaul.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 had a 1% violation on 30 August for trashrack raking.  Was out of service from 0700 until 0850 on 31 August for STS inspections.   Went out of service at 0910 on 01 September due to possible rotor failure.

    - Unit 12 had a 1% violation on 30 August for trashrack raking.  Was out of service from 0853 until 1135 on 31 August for STS inspections.

    - Unit 13 was out of service from 1135 until 1400 on 31 August for STS inspections.

    - Unit 14 was out of service from 1400 until 1630 on 31 August for STS inspections.

    - Unit 15 remains out of service for main unit circuit breaker replacement and annual maintenance.

    - Unit 16 remains out of service for main unit circuit breaker replacement and annual maintenance.

    - Unit 17 had a 1% violation starting at 0905 for trashrack raking and was out of service from 1128 until 1400 on 01 September for STS inspections.

    - Unit 18 had a 1% violation on 30 August for trashrack raking.   Was out of service from 0915 until 1125 on 01 September for STS inspections.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV1-1- closed for cleaning from 1610 until 1617 on 29 August.

    - FV3-9- closed for cleaning from 1530 until 1545 on 01 September.

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 8/31 | 770 |  |
| 12 | 8/31 | 409 |  |
| 13 | 8/31 | 123 |  |
| 14 | 8/31 | 128 |  |
| 15 | 9/1 | 339 |  |
| 16 |  |  | Out for MUCB replacement |
| 17 | 9/1 | 191 |  |
| 18 | 9/1 | 662 |  |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

    - Unit 6 draft tube was dewatered on 29 August.  Biologists released one sturgeon, one lamprey, and one catfish alive and in good condition.

    - B2CC was dewatered on 31 August.  No fish were found.

- RESEARCH

  - CRITFC.  Chinook sampling voluntarily suspended until water temperatures drop below 70.0F.  Mandatory steelhead sampling continues.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.  Washington Shore and BI ramp continue to operate.

  - PSMFC.  No fallbacks or kelts were observed crossing the separator bars this week.

  - Univ of Idaho.  Trapping allowed four days/week.  See 6.1.5

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

  - WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island continues.

- FISHWAYS

  - Project biologists inspected 28 August through 03 September.  NOAA Fisheries inspected on 31 August.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | B-Branch | North gate closed. | Separated from shaft | See 6.1.4 |  |
| 8/28 | B-Branch entrance | FG3-26 not in correct position. | System in manual. | Operators corrected |  |
| 8/28 | Cascades Is. entrance | FG6-13 not in correct position. | System in manual. | Operators corrected |  |
| 8/28-31 | Spill bay 16 | Dogged at 3.0’ | Lifting beam out of alignment. | See 6.2.2 |  |
| 9/1-3 | A-Branch | Construction within 50’ of the fishway | Lack of proper coordination. | Reminded the Project of the need to coordinate such activities with the Fisheries Office. Work currently being performed in the evening hours. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 8/28 | 71.1 | 71.1 | 71.2 |
| 8/29 | 70.8 | 70.7 | 70.9 |
| 8/30 | 70.5 | 70.4 | 70.5 |
| 8/31 | 70.4 | 70.4 | 70.5 |
| 9/01 | 70.7 | 70.6 | 70.8 |
| 9/02 | 70.5 | 70.4 | 70.5 |
| 9/03 | 70.1 | 70.0 | 70.3 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 02 September.  Two PH1 PCC sensors are scheduled for replacement on 12-13 September.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods started on 15 August with Units 15/16.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.

    - B-Branch south entrance gate remains open to compensate for the north entrance gate.

    - The AFF is open for salmonid trapping four days a week, from 0600 until 1000, until temperatures drop to 69.5F (as per the FPP).   Due to fish counts exceeding 15,000 at the WS, no more than three picket leads will be down until further notice.

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

    - Due to concerns about safety, Bay 16 has been dogged off at two dogs (3.0’) until spill ends on 31 August.  The lifting beam is out of alignment with the gate.  The rest of the spillway remains in auto and will compensate for the extra .5’ of flow through Bay 16.

    - The B2CC closed at 0917 on 31 August for the season.

  - Upcoming Events.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A 30 August teletype requests that outflows from Bonneville and The Dalles be maintained as low and as constant as possible from 0700 until 1130 on 05 September to reduce currents in the river during the Columbia River Cross Channel Swim at Hood River

  - A 31 August teletype states Bonneville project may close spill bay 16 due to lifting beam safety concerns.  The project will adjust for the flow that would normally go through bay 16 by opening bays 14 and 15 to 3.0’.

  - A 02 September teletype requests Bonneville to maintain a forebay of 75.0-76.5’ msl from 0600 on 06 September until 1800 on 10 September.  This is to limit wear and tear on tribal gillnet equipment.

  - The 2005/06 winter maintenance schedule will be available, in DRAFT form, by the September FPOM mtg.

JAMES R. MAHAR, P.E.

Operations Manager

//S/