### CENWP-OP-B                                                                                                                                  11 September 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 37 of 2005, which covers the period from 04 through 10 September 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 81.2 to 95.3 kcfs.  Daily average project tailwater elevation ranged from 8.2’ to 9.3’ msl.  Daily average powerhouse forebay elevation ranged from 75.1’ to 76.2’ msl.  Daily average river temperature ranged from 69 to 70F.  Secchi disk measurements averaged 5.5 to 7.0 feet.

  - Daily average spill ranged from 1.4 to 1.7 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 6 remains out of service for a five-year overhaul.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service due to a possible rotor failure.

    - Unit 15 remains out of service for main unit circuit breaker replacement and annual maintenance.

    - Unit 16 remains out of service for main unit circuit breaker replacement and annual maintenance.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting week

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Chinook sampling voluntarily suspended until water temperatures drop below 70.0F.  Mandatory steelhead sampling continues.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.  Washington Shore and BI ramp continue to operate.

  - NOAA Fish PIT tag.  Tagging to start 13 September.

  - PSMFC.  No fallbacks or kelts were observed crossing the separator bars this week.

  - Univ of Idaho.  Trapping allowed four days/week.  See 6.1.5

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

  - WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island continues.

- FISHWAYS

  - Project biologists inspected 04 through 10 September.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | B-Branch | North gate closed. | Separated from shaft | See 6.1.4 |  |
| 9/5 | B-Branch | Gauge reading <1.0’ | Unknown | No action taken, rest of BI ok. |  |
| 9/5, 9/7, 9/9 | Weir 37 | Reading <1.0’> | Unknown | No action taken. Weir 38 ok. |  |
| 9/6 | A-Branch | Construction within 50’ of the fishway | Lack of proper coordination. | Reminded the Project of the need to coordinate activities with Project Fisheries. Work currently done during after 1700. |  |
| 9/7 | CI | Differential low. | System in manual | Operators adjusted valves. |  |
| 9/8, 9/10 | A-Branch | FG3-3 not in correct position for TW | Diffuser in manual, won’t move. | Operators TR’d |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.  The AFF is measured inside the lab at the fish return.

| Date | WA Shore Average | Bradford Is Average | ##### AFF exit max |
| --- | --- | --- | --- |
| 9/04 | 70.0 | 69.8 | 70.0 |
| 9/05 | 69.8 | 69.6 | 69.8 |
| 9/06 | 69.8 | 69.7 | 69.9 |
| 9/07 | 70.0 | 69.8 | 70.0 |
| 9/08 | 70.1 | 69.9 | 70.2 |
| 9/09 | 69.3 | 69.2 | 69.3 |
| 9/10 | 68.7 | 68.3 | 68.6 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 08 September.  Two PH1 PCC sensors are scheduled for replacement on 12-13 September.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation scheduled for late summer 2005.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods started on 15 August with Units 15/16.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.

    - B-Branch north gate has separated from the shaft.  The south gate compensates when possible.

    - The AFF is open for salmonid trapping four days a week, from 0600 until 1000, until temperatures drop to 69.5F (as per the FPP).   Due to fish counts exceeding 15,000 at the WS, no more than three picket leads will be down until further notice.

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

  - Upcoming Events.

    - The JMF will go to bypass at 0700 on 31 October.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A 30 August teletype requests that outflows from Bonneville and The Dalles be maintained as low and as constant as possible from 0700 until 1130 on 05 September to reduce currents in the river during the Columbia River Cross Channel Swim at Hood River

  - A 02 September teletype requests Bonneville to maintain a forebay of 75.0-76.5’ msl from 0600 on 06 September until 1800 on 10 September.  This is to limit wear and tear on tribal gillnet equipment.

  - A 09 September teletype requests Bonneville to maintain a forebay of 75.0-76.5’ msl from 0600 on 12 September until 1800 on 16 September.  This is to limit wear and tear on tribal gillnet equipment.

  - The 2005/06 winter maintenance schedule, FPP Appendix G draft changes and the addition of a FPP Appendix for JMF protocols was distributed, in DRAFT form, at the 08 September FPOM.

JAMES R. MAHAR, P.E.

Operations Manager

//S/