### CENWP-OP-B                                                                                                                                  25 September 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 39 of 2005, which covers the period from 18 through 24 September 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 74.9 to 111.9 kcfs.  Daily average project tailwater elevation ranged from 8.1’ to 10.4’ msl.  Daily average powerhouse forebay elevation ranged from 76.1’ to 76.2’ msl.  Daily average river temperature ranged from 66 to 67F.  Secchi disk measurements averaged 7.0 feet.

  - Daily average spill ranged from 1.3 to 1.4 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 6 remains out of service for a five-year overhaul.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service due to a possible rotor failure.

    - Unit 15 returned to service at 1624 on 19 September.  Unit 15 was out of service from 1639 until 1651 on 22 September due to an accidental relay trip.

    - Unit 16 returned to service at 1636 on 19 September and was out of service from 1713 on 19 September until 1033 on 20 September due to exciter trouble.

    - Unit 17 went out of service at 0439 on 19 September for main unit circuit breaker replacement and T-12 switching.

    - Unit 18 went out of service at 0439 on 19 September for main unit circuit breaker replacement and t-12 switching.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F1 was out of service from 1639 until 1657 on 22 September due to an accidental relay trip.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV3-9 was closed from 1603 until 1620 on 19 September.

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

    - On 20 September, fish biologists removed 30 live sturgeon, six catfish and one peamouth from the Unit 11 draft tube.  All fish were released alive at the Hamilton Island boat launch.

- RESEARCH

  - CRITFC.  Sampling two days a week continues.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish Lamprey.  Washington Shore ramp to shut down on 27 September.  The BI ramp still operates.

  - NOAA Fish PIT tag.  Tagging started 13 September.

  - PSMFC.  Two fallback salmon and one steelhead were observed crossing the separator bars this week.  Loss of power at the facility on 22 September (see 6.2.3)

  - Univ of Idaho.  Trapping and tagging continues.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

  - WDFW and ODFW.  Tule counting at Washington Shore and Bradford Island continues.

- FISHWAYS

  - Project biologists inspected 18 through 24 September.  NOAA Fisheries inspected on 22 September.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | B-Branch | North gate closed | Separated from shaft | See 6.1.4 |  |
| 9/18-19, 21, 24 | Weirs 37/38 | Reading <1.0> | Unknown | Adjusted Valve 2 in the AFF |  |
| 9/20, 9/24 | A-Branch | FG3-3 not in correct position for TW. | Diffuser in manual. Cannot be adjusted. | No action taken. Repairs scheduled for Winter 05/06 |  |
| 9/21 | Cascades Island | North entrance gate in incorrect position. | System in manual. | Operators adjusted. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.

| Date | WA Shore Average | Bradford Is Average |
| --- | --- | --- |
| 9/18 | 66.4 | 66.3 |
| 9/19 | 66.5 | 66.3 |
| 9/20 | 66.4 | 66.4 |
| 9/21 | 66.1 | 65.9 |
| 9/22 | 65.7 | 65.5 |
| 9/23 | 65.7 | 65.5 |
| 9/24 | 65.5 | 65.3 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 24 September.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation sometime before winter.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods continue with Units 17/18.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.

    - B-Branch north gate has separated from the shaft.  The south gate compensates when possible.

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

    - DSM1 continues to flow south.

    - At 1639 on 22 September, electricians accidentally tripped a relay, resulting in a loss of power to several PH2 units, the visitor center and the monitoring facility.  The loss of power at the JMF resulted in the upper switchgate automatically moving to bypass.  Power was restored by 1700.

  - Upcoming Events.

    - The JMF will go to bypass at 0700 on 31 October.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP – Nothing to report this week.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A 16 September teletype requests Bonneville maintain a forebay of 75.0-76.5’ msl from 0600 on 19 September until 1800 on 23 September.  This is to limit wear and tear on tribal gillnet equipment.

JAMES R. MAHAR, P.E.

Operations Manager

//S/