### CENWP-OP-B                                                                                                                                  24 October 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 43 of 2005, which covers the period from 16 through 23 October 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 90.2 to 123.2 kcfs.  Daily average project tailwater elevation ranged from 9.3’ to 12.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.6’ to 74.9’ msl.  Daily average river temperature ranged from 61 to 62F.  Secchi disk measurements averaged 7.0 feet.

  - Daily average spill ranged from 1.1 to 1.3 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 6” during daylight hours.

    - Spill bay 18 was operated out of FPP criteria from 1259 until 1317 on 18 October for gate testing.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 6 remains out of service for a five-year overhaul.

    - Unit 10 remains out of service for gantry crane three construction.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 12 remains out of service for MUCB replacement.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

    - F1 was out of service from 0845 until 1001 on 21 October for switching activities.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week

    - FV3-9 - closed from 0840 until 0910 on 17 October for cleaning.

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1 | 10/17 | 682 |  |
| 3 | 10/17 | 683 |  |

Table 1.  STS/VBS Inspections.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampling two days a week continues.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fish PIT tag.  Tagging finished.

  - PSMFC.  Ten adult salmon were observed crossing the separator bars this week.

  - WDFW Fish Counting.  16-hr visual counting at Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 16-23 October.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 N PCC | Velocity <1.5 fps | Slow water | Normal condition. |  |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | B-Branch | North gate closed | Separated from shaft | See 6.1.4 |  |
| 10/16 | PH1 ITS | Chain gates not set correctly. |  | Chain gates reset on 10/17. |  |
| 10/16, 10/20 | Weir 37 | Reading <1.0’> | Unknown | Operators blow off screen |  |
| 10/16 | B-Branch | Differential high or low | System in manual | Operators adjusted FV4-4, FV4-3 |  |
| 10/20-22 | Weir 38 | Reading <1.0’> | Unknown/Weir 37 | No action taken |  |
| 10/21 | Fish Unit 1 | OOS without coordination | Switching activities |  |  |
| 10/22 | BI, A and B branch gauge | Reading <1.0’> | Low forebay | Operators to check FV3-9 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island as well as at the junction of the UMT and the main ladder at Washington shore.

| ##### Date | WA Shore Average | Bradford Is Average |
| --- | --- | --- |
| 10/16 | 62.4 | 62.4 |
| 10/17 | 62.4 | 62.4 |
| 10/18 | 62.4 | 62.4 |
| 10/19 | 62.4 | 62.4 |
| 10/20 | 62.3 | 62.4 |
| 10/21 | 61.8 | 61.6 |
| 10/22 | 61.2 | 61.1 |

Table 3.  Bonneville Fishway temperatures.

  - Sensor Calibration.  Calibration was checked on 20 October.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Installation is planned for winter 05/06.

  - B2 Fish Unit Trash rake.  Delivery and installation sometime before winter.

  - B2 VBS modifications.  Gatewell modifications to begin in Unit 13 starting early November.

  - Bradford Island Adult PIT Tag Detectors.  Installation scheduled for winter 05/06.

  - Main Unit Circuit Breaker.  Mods continue on Units 11/12.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Site visit occurred on 11 October.

- FISHWAY STATUS

  - Adult Fishways.

    - B-Branch fishway PLC is in manual.  Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.  FG6-11 is used to compensate.

    - A-branch has been reprogrammed.  FG3-4 remains out of service until winter 2005/06.

    - B-Branch north gate has separated from the shaft.  The south gate compensates when possible.

    - PH1 ITS Chain gates 3B, 3C, and 7A were set to 72.0’ msl at 0840 on 17 October.

  - Juvenile Fishways.

    - DSM2 screen sweeps are exercised on Sunday evenings.

  - Upcoming Events.

    - The JMF will go to bypass at 0700 on 31 October.

    - The UMT is scheduled to go OOS (to accommodate VBS modification work) on 31 October.

    - Cascades Island is scheduled to open on 31 October.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report

- TELETYPES AND OTHER NOTEWORTHY ITEMS.  Nothing to report

JAMES R. MAHAR, P.E.

Operations Manager

//S/