### CENWP-OP-B                                                                                                                                  19 December 2005

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 51 of 2005, which covers the period from 11 through 17 December 2005.

- OPERATION SUMMARY

  - Daily average river flows ranged from 115.3 to 145.8 kcfs.  Daily average project tailwater elevation ranged from 11.5’ to 13.2’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.6’ msl.  Daily average river temperature ranged from 41 to 44F.  Secchi disk measurements averaged 7.0 feet.

  - Daily average spill was 0.5 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service from 0514 until 1516 on 16 December due to power supply governor problem.

    - Unit 4 was out of service from 0930 until 1516 on 16 December due to potential relay protection problem.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 12 was out of service from 0714 until 0932 on 16 December for STS removal.

    - Unit 13 remains out of service for VBS mods and a four-year overhaul.

    - Unit 14 was out of service from 0152 until 1540 on 15 December due to a STS failure.

    - Unit 15 was out of service from 1025 until 1201 on 16 December for STS removal.

    - Unit 16 was out of service from 1129 until 1357 on 15 December for STS removal.

    - Unit 17 was out of service from 0745 until 0920 on 15 December for STS removal.

    - Unit 18 was out of service from 0955 until 1126 on 15 December for STS removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 1800-0500 nightly due to aquatic vegetation and excessive drawdowns.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this reporting week.

  - STS/VBS Inspections.  No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle/Normandeau.  Sensor fish postponed until further notice.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - WDFW Chum.  Trapping and tagging concluded on 15 December.

  - WDFW Fish Counting.  16-hr video counting at Cascades Island, Washington Shore and Bradford Island.

- FISHWAYS

  - Project biologists inspected 12 through 16 December.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All Week | DSM2 | Airburst OOS | PLC failure | TR sent to electricians. | 06-8326 |
| All Week | B-Branch | North gate closed | Separated from shaft | See 6.1.4 |  |
| 12/12-13 | Weir 38 | Reading <1.0> |  |  |  |
| 12/13-16 | Weir 37 | Reading <1.0> | Clogged trashrack | Riggers cleaned trashrack. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  Calibration was not checked this week.  PH1 collection channel and B-Branch are out of service.  B-Branch and Cascades Island are out of calibration until sensors can be replaced and recalibrated.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B2CC PIT Tag Detector.  Demolition and construction continue.

  - B2 VBS modifications.  Gatewell VBS slot modifications continue on Unit 13.

  - Bradford Island Adult PIT Tag Detectors.  Installation continued this week.

  - Main Unit Circuit Breaker.  Mods continue on Units 13.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  No new updates.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island PLC is in manual.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

  - Juvenile Fishways.

    - DSM2 screen cleaners in auto and on three hour cleaning cycles.  Airburst system in manual.

    - PH2 and Unit 3 STS’s removed on 15 and 16 December.

  - Upcoming Events.

    - PH1 DSM dewatering on 20 December.

    - PH2 DSM dewatering on 20 December.

    - Two-mile pipe inspection on 20-21 December.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 10 November requests hard tailwater constraint of 11.3’ to 11.7’ between 0700 and 1900 daily and no less than 11.3’ at any time.  This is to facilitate chum spawning around Ives and Pierce Islands.

JAMES R. MAHAR, P.E.

Operations Manager

//S/