### CENWP-OP-B                                                                                                                                  23 January 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 03 of 2006, which covers the period from 15 through 21 January 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 196.2 to 254.6 kcfs.  Daily average project tailwater elevation ranged from 19.5’ to 22.6’ msl.  Daily average powerhouse forebay elevation ranged from 73.3’ to 74.5’ msl.  Daily average river temperature was 42F.  Secchi disk measurements averaged 3.0 to 4.0 feet.

  - Daily average spill averaged 0.5 to 44.3 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.   Due to high flows, the Project spilled more than attraction flow from 17-20 January.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 13 remains out of service for VBS mods and a four-year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F2 returned to service at 1034 on 18 January.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves remain closed this reporting week.

    - FV1-1- for BI fishway overhaul.

    - FV3-7- for BI fishway overhaul.

    - FV3-9- for BI fishway overhaul.

    - FV4-3- for BI fishway overhaul.

    - FV4-4- for BI fishway overhaul.

  - STS/VBS Inspections.  STSs/VBSs have been removed for the winter.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

    - Biologists and FFU removed five juvenile chinook, one juvenile steelhead, one adult unclipped steelhead, one sculpin, three dead adult unknown salmonids from the B-Branch entrance on 20 January.

- RESEARCH

  - Battelle/Normandeau.  Sensor fish postponed until summer.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - USGS.  Set lining and angling in forebay as part of the BI remediation.

  - WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.

- FISHWAYS

  - Project biologists inspected 17-19 and 21 January.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |
| 1/17-19 | PH2 PCC | Floating orifice gate submerged. | Unknown. Could be stuck. | Riggers notified. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  PH1 collection channel and B-Branch are out of service.  Cascades Island is out of calibration until sensors can be replaced and recalibrated.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in February 2006.

  - B2CC PIT Tag Detector.  Concrete placement has been impacted due to high tailwater.

  - B2 VBS modifications.  Moving to Unit 12 the week of 23 January.

  - B2 Fish Unit trashrake.  According to the structural crew, the new rake does not work as well as the old rake.  The new rake is not being used at this time.

  - Bradford Island Adult PIT Tag Detectors.  Installation continues.

  - Main Unit Circuit Breaker.  Mods are completed.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Nothing new to report.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island PLC is in manual.  New sensors will be installed and calibrated before fish passage season for both CI and B-Branch.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

    - Bradford Island fishway remains out of service until late February.

    - As of 06 January, FG3-3 and FG3-4 are able to return to service when BI returns.

    - PH2 PCC floating orifice gate stab plates were installed the week of 05 January.  Criteria is not maintained with just stab plates and one fish unit.  Diffusers and entrance gates have been adjusted to maintain a 1.0’ head over the monolith entrances.

    - Electricians are removing electrical hardware associated with PH1 PCC OG/SGs.

  - Juvenile Fishways.

    - DSM1 will remain out of service until 15 September.

    - DSM2 will remain out of service until late February.

  - Upcoming Events.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January.  This operation is to provide chum incubation flows below Bonneville.

  - A teletype issued on 20 January requests a maximum tailwater of 21.0’ from 0700 on 21 January until 2100 on 22 January.  This is to facilitate concrete work at the B2CC through the weekend.

JAMES R. MAHAR, P.E.

Operations Manager

//S/