### CENWP-OP-B                                                                                                                                  12 February 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 06 of 2006, which covers the period from 05 through 11 February 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 165.5 to 205.4 kcfs.  Daily average project tailwater elevation ranged from 15.3’ to 18.9’ msl.  Daily average powerhouse forebay elevation ranged from 72.5’ to 74.9’ msl.  Daily average river temperature ranged from 41 to 42F.  Secchi disk measurements averaged 3.5 to 5.0 feet.

  - Daily average spill averaged 0.5 to 0.6 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 12 remains out of service for VBS modifications.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was on standby from 1311 until 1605 on 05 February, to float trash.

    - F2 was on standby from 1308 until 1613 on 05 February, to float trash.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves remain closed this reporting week.

    - FV1-1- for BI fishway overhaul.

    - FV3-7- for BI fishway overhaul.

    - FV3-9- for BI fishway overhaul.

    - FV4-3/ 4-4- for BI fishway overhaul.

  - STS/VBS Inspections.  STSs/VBSs have been removed for the winter.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle/Normandeau.  Sensor fish testing scheduled for mid to late March.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp to begin on 06 February.

  - USGS.  Set lining and angling in forebay as part of the BI remediation will resume in mid-February.

  - WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.

- FISHWAYS

  - Project biologists inspected 7-9 February.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper install. | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |
| 2/06 | Weir 37/38 | Reading <1.0’ | Change in FB elev. | No response |  |
| 2/07 | Cascades Is. | FG6-9 open | Computer in manual | Operators closed. |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  PH1 collection channel and B-Branch are out of service.  Cascades Island is out of calibration until sensors can be replaced and recalibrated.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in 2006.

  - B2CC PIT Tag Detector.  Construction continues.

  - B2 VBS modifications.  Mods continue on Unit 12.

  - B2 Fish Unit trashrake.  According to the structural crew, the new rake does not work as well as the old rake.  The new rake is not being used at this time.

  - B2 Follow-on.  Flume invert measurements ongoing.

  - Bradford Island Adult PIT Tag Detectors.  Installation continues.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Pipe excavation began on 06 February.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island PLC is in manual.  New sensors will be installed and calibrated before fish passage season for both CI and B-Branch.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - DSM2 remains out of service until late February.

  - Upcoming Events.

    - BI returns to service on 23 February.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January.  This operation is to provide chum incubation flows below Bonneville.

JAMES R. MAHAR, P.E.

Operations Manager

//S/