### CENWP-OP-B                                                                                                                                  21 February 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 07 of 2006, which covers the period from 12 through 18 February 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 161.5 to 196.3 kcfs.  Daily average project tailwater elevation ranged from 15.0’ to 16.9’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.3’ msl.  Daily average river temperature ranged from 39 to 41F.  Secchi disk measurements averaged 4.0 to 6.2 feet.

  - Daily average spill averaged 0.6 to 0.7 kcfs.   Spill Bay 1, which supplies attraction flow for Cascades Island, is open 6” during daylight hours.

    - Annual spill bay testing occurred from 0856 until 0950 on 13 February.

  - Unit operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 9 was out of service from 1352 until 1559 on 16 February for an exciter fan replacement.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 12 remains out of service for VBS modifications.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 0824 until 1025 on 14 February to facilitate the winter ROV inspection.

    - F2 was out of service from 0825 until 1025 on 14 February to facilitate the winter ROV inspection.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves remain closed this reporting week.

    - FV1-1 closed for BI fishway overhaul.

    - FV3-7 closed for BI fishway overhaul.

    - FV3-9 closed for BI fishway overhaul.

    - FV4-3/ 4-4 closed for BI fishway overhaul.

    - FV5-3/5-4 closed from 1050 until 1220 on 14 February for the CI entrance ROV inspection.

    - FV5-9 closed from 1028 until 1220 on 14 February for the CI entrance ROV inspection.

    - FV6-9 closed from 0832 until 1020 on 14 February for the PH2 PCC ROV inspection.

  - STS/VBS Inspections.  STSs/VBSs have been removed for the winter.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - Battelle/Normandeau.  Sensor fish testing scheduled for mid to late March.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp to begin on 06 February.

  - USGS.  Set lining and angling in forebay as part of the BI remediation resumed on 14 February.

  - WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.

- FISHWAYS

  - Project biologists inspected 12-14, and 16 February.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Temperatures are not recorded during the winter maintenance period.

  - Sensor Calibration.  PH1 collection channel and B-Branch are out of service.  Cascades Island is out of calibration until sensors can be replaced and recalibrated.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in 2006.

  - B2CC PIT Tag Detector.  Construction continues.  The antenna has arrived and has been assembled in PH2.

  - B2 VBS modifications.  Mods continue on Unit 12.  VBS delivery is scheduled for the week of 27 February.

  - B2 Fish Unit trashrake.  According to the structural crew, the new rake does not work as well as the old rake.  The new rake is not being used at this time.

  - B2 Follow-on.  Flume invert measurements continued 12-15 February.

  - Bradford Island Adult PIT Tag Detectors.  Walk through occurred on 17 February.  Another walk through is scheduled for 20 February.  PSMFC testing to begin 21 February.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Pipe excavation and shoring continues.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island PLC is in manual.  New sensors are scheduled to be installed and calibrated before fish passage season for both CI and B-Branch.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

    - SLADDs and SLEDs are installed at PH2.  Installation at PH1 and the Main Dam fishways to occur throughout the month.

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - DSM2 remains out of service until late February.

  - Upcoming Events.

    - BI returns to service on 23 February.

    - Video counting at BI to begin on 23 February.

    - Spring Creek release scheduled for 02 March.

    - B2CC scheduled to open for Spring Creek fish passage from 03-07 March.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January.  This operation is to provide chum incubation flows below Bonneville.

JAMES R. MAHAR, P.E.

Operations Manager

//S/