### CENWP-OP-B                                                                                                                                  20 March 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 11 of 2006, which covers the period from 12 through 18 March 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 124.8 to 188.5 kcfs.  Daily average project tailwater elevation ranged from 12.4’ to 16.0’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.3 msl.  Daily average river temperature ranged from 41 to 43F.  Secchi disk measurements averaged 5.0 to 6.0 feet.

  - Daily average spill averaged 1.3 to 1.4 kcfs.   Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service due to a rotor failure.

    - Unit 12 remains out of service for VBS modifications.

    - Unit 13 was out of service from 1157 until 1631on 16 March due to STS screen cord being cut.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.  Drawdowns are measured daily on Unit 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV1-1 closed for cleaning from 1601 until 1616 on 14 March.

    - FV5-9 closed for cleaning from 1610 until 1650 on 14 March.

  - STS/VBS Inspections.   The following STSs/VBSs were installed this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 3/15 |  |  |
| 12 |  |  |  |
| 13 | 3/2 |  |  |
| 14 | 2/28 |  |  |
| 15 | 2/28 |  |  |
| 16 | 2/28 |  |  |
| 17 | 3/3 |  |  |
| 18 | 3/1 |  |  |

Table 1.  STS Installation Dates.

  - Dewatering and Fish Salvage.  The following dewatering or salvage activities occurred this reporting week.

2.3.1      On 13 March, the following were removed from Unit 11 tail logs: 14 sturgeon, three sculpin,

one bass, and one bullhead.  All were released in good condition.

- RESEARCH

  - Battelle/Normandeau.  Sensor fish testing scheduled to begin 23 March.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries lamprey.  Permanent installation of the BI AWS lamprey ramp completed.

  - PSMFC.  Three adult steelhead were observed crossing the separator bars this week.

  - USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

  - WDFW Fish Counting.  16-hr video counting at Cascades Island and Washington Shore.

- FISHWAYS

  - Project biologists inspected 12 March – 18 March.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |
| All week | PH1 CCH Diffusers | FG2-22A closed, 2-19 stuck half open | Unknown. Failed during water up. | Will repair in 07/08 |  |
| 3/12, 3/18 | B-branch | Staff gauge < 1.0 | Unknown |  |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 3/12 | 41.8 | 42.0 |
| 3/13 | 42.2 | 42.4 |
| 3/14 | 42.4 | 42.5 |
| 3/15 | 42.5 | 42.7 |
| 3/16 | 42.7 | 42.9 |
| 3/17 | 42.7 | 43.0 |
| 3/18 | 42.8 | 42.9 |

  - Sensor Calibration.  Calibration was checked on 18 March.  Cascades Island and B-Branch need recalibration.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in 2006.

  - B2CC PIT Tag Detector.  Installation scheduled for 23 March.

  - B2 VBS modifications.  Mods continue on Unit 12.

  - B2 Fish Unit trash rake.  According to the structural crew, the new rake does not work as well as the old rake and is not being used at this time.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Construction continues.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island PLC’s are in manual.

    - New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

    - SLADDs and SLEDs are installed at all fishway entrances.

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - Unit 11 STS’s installed on 15 March.

- HAZMAT, SPILLS AND CLEANUP

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype issued on 31 December authorizes a minimum tailwater of 11.5’ for all hours, starting at 0000 on 01 January until further notice.  This operation is to provide chum incubation flows below Bonneville.

  - The navigation lock was taken out of service for annual maintenance at 0600 on 11 March.

JAMES R. MAHAR, P.E.

Operations Manager

//S/