### CENWP-OP-B                                                                                                                                  08 May 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 18 of 2006, which covers the period from 30 April through 06 May 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 296.6 to 382.8 kcfs.  Daily average project tailwater elevation ranged from 22.2’ to 26.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.6 msl.  Daily average river temperature ranged from 52 to 54F.  Secchi disk measurements averaged 2.5 to 3.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 95.0 to 159.9 kcfs.

  - Unit Operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service on 30 April from 1533 to 1756 due to a governor pressure switch failure.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 went out of service at 0714 on 24 April for bearing alignment.

    - Unit 12 had a 1% violation on 1 May for STS inspection.

    - Unit 12 was out of service for STS repair from 0857 to 1158 to on 2 May.

    - Unit 14 had a 1% violation on 1 May for STS inspection.

    - Unit 15 had a 1% violation on 1 May for STS inspection.

    - Unit 16 had a 1% violation on 1 May for STS inspection.

    - Unit 18 had a 1% violation on 2 May for STS inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Fish Units 1 and 2 were run at reduced loads while repairing floating orifice gates from 1006 to 1140 and from 1500 to 1608 on 1 May, from 0731 to 0828 and 1303 to 1425 on 2 May, from 0905 to 0951 on 3 May, and from 1021 to 1130 on 4 May.   See 6.1.4.

    - Fish Unit 2 was out of service from 1224 to 1638 on 6 May due to governor problems.

  - Gatewell drawdowns are measured on Wednesdays.  VBS drawdowns are measured daily on Units 12, 13, and 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV4-3 and FV4-4 were closed to pass trash from the forebay through spillbay 18 from 1203 to 1245 on 1 May.

    - FV3-7 was closed for cleaning from 1455 to 1600 on 4 May.

  - STS/VBS Inspections.   The following  STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 5/1 | 138 |  |
| 12 | 5/1 | 335 | Pulled STS A to repair latch wire. |
| 13 | 5/1 | 615 |  |
| 14 | 5/1 | 614 |  |
| 15 | 5/1 | 615 |  |
| 16 | 5/1 | 614 |  |
| 17 | 5/2 | 614 |  |
| 18 | 5/2 | 615 |  |

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week:

- RESEARCH

  - CRITFC.  Sampling adult fish in the AFF.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations continue.

  - NOAA Fisheries - juvenile salmonids.  Sampling juvenile salmonids to determine prevalence of pathogens.

  - NOAA Fisheries - barge vs. bypass.   Assessment of the health of hatchery salmon relative to in-river and transportation life-histories.

  - PSMFC.  Three adult steelhead were observed crossing the separator bars this week.  575 clipped yearling chinook and 25 coho were collected for NOAA researchers this reporting week.

  - U of I.  Radio tagging of spring chinook for SLED evaluation continues in the AFF.

  - USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

  - WDFW Fish Counting.  Visual fish counting continues.

  - WDFW/ODFW.  Sea lion hazing from boats continues.

- FISHWAYS

  - Project biologists inspected 30 April – 06 May.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |
| All week | PH1 CCH Diffusers | FG2-22A closed, 2-19 stuck half open | Unknown. Failed during water up. | Will repair in 07/08 |  |
| All week | SUE and SDE | Gate < 13’ | Unknown |  |  |
| 5/2 and 5/6 | PH2 entrances | Differential too high | Orifice gate repair | Fish units adjusted |  |
| 5/3 | PH1 entrances | Differential too low | Electrical problem | Repaired |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 4/30 | 52.2 | 52.4 |
| 5/1 | 52.3 | 52.4 |
| 5/2 | 52.8 | 52.9 |
| 5/3 | 53.2 | 53.4 |
| 5/4 | 53.8 | 54.0 |
| 5/5 | 54.2 | 54.3 |
| 5/6 | 54.1 | 54.3 |

  - Sensor Calibration.  Calibration was checked on 06 May.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in 2006.

  - B2CC PIT Tag Detector.  Construction complete.  Opened for the season at 0815 on 13 April.

  - B2 VBS modifications.  VBS delivery occurred on 3 April.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Construction continues.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island PLC’s are in manual.

    - New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

    - Floating Orifice Gates at PH2 have been repaired and stab plates installed.  See 1.4.1

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - The B2CC remains open.

- HAZMAT, SPILLS AND CLEANUP - Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype was issued on 2 May stating that spillbays 6 and 11 will be unhooked and dogged off at 2.9’ on 3 May to allow for placement of acoustic equipment on spillway piernoses.

  - A teletype was issued on 5 May setting priority by project for voluntary and involuntary spill to limit total dissolved gas.

JAMES R. MAHAR, P.E.

Operations Manager

//S/