### CENWP-OP-B                                                                                                                                  15 May 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 19 of 2006, which covers the period from 07 through 13 May 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 284.2 to 320.8 kcfs.  Daily average project tailwater elevation ranged from 21.3’ to 23.3’ msl.  Daily average powerhouse forebay elevation ranged from 73.0’ to 75.3 msl.  Daily average river temperature ranged from 54 to 55F.  Secchi disk measurements averaged 2.5 to 4.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 84.4 to 96.3 kcfs.

  - Unit Operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 went out of service at 0714 on 24 April for bearing alignment.

    - Unit 18 was out of service from 0809 to 0907 due to high stator temperature.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays.  VBS drawdowns are measured daily on Units 12, 13, and 17.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this reporting week.

    - FV5-9 was closed for cleaning from 1549 to 1605 on 11 May.

  - STS/VBS Inspections.   No STSs/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or salvage activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampling adult fish in the AFF.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Fish Field Unit.  Sea lion observation and acoustic deterrent evaluations continue.

  - NOAA Fisheries - juvenile salmonids.  Sampling juvenile salmonids to determine prevalence of pathogens.

  - NOAA Fisheries - barge vs. bypass.   Assessment of the health differences between barged and bypassed hatchery salmon.

  - PSMFC.  Three kelts were removed from the separator bars this week.  Ten steelhead and seven salmon were observed crossing the separator bars.  There were 336 clipped yearling chinook and 25 coho collected for NOAA researchers this reporting week.

  - U of I.  Radio tagging of spring chinook for SLED evaluation continues in the AFF.

  - USDA Wildlife Services.  Sea lion hazing continues using 15mm cracker/screamer shells and rubber bullets.

  - WDFW Fish Counting.  Visual fish counting continues.

  - WDFW/ODFW.  Sea lion hazing from boats continues.

- FISHWAYS

  - Project biologists inspected 07 - 13 May.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 SCCH | Velocity <1.5 fps | Improper installation | Will repair in 06/07 |  |
| All week | Cascades Is. | FG6-12 closed | Bent shaft | Will repair in 06/07 |  |
| All week | PH1 CCH Diffusers | FG2-22A closed, 2-19 stuck half open | Unknown. Failed during water up. | Will repair in 07/08 |  |
| All week | SUE | Gate < 13’ | Unknown |  |  |

Table 2.  FPP Out of Criteria items.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/7 | 53.9 | 54.0 |
| 5/8 | 53.7 | 53.8 |
| 5/9 | 53.9 | 54.1 |
| 5/10 | 54.4 | 54.5 |
| 5/11 | 54.9 | 55.0 |
| 5/12 | 55.0 | 55.0 |
| 5/13 | 55.1 | 55.2 |

  - Sensor Calibration.  Calibration was checked on 13 May.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  A letter report is expected in 2006.

  - B2CC PIT Tag Detector.  Construction complete.  Opened for the season at 0815 on 13 April.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Construction continues.

- FISHWAY STATUS

  - Adult Fishways.

    - Bradford Island and Cascades Island PLC’s are in manual.

    - New sensors for B-branch and Cascades Island tailrace, entrance and ladder have been installed.

    - Cascades Island diffuser FG6-12 has a bent shaft and remains out of service until winter 2006/07.

    - Floating Orifice Gates at PH2 have been repaired and stab plates installed.  See 1.4.1

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - The B2CC remains open.

    - Approximately 225 juvenile salmonid mortalities were discovered on Units 13 and 17 VBSs.  Drawdown criteria for cleaning were reduced and the situation is being monitored.

- HAZMAT, SPILLS AND CLEANUP - Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype was issued on 12 May setting priority by project for voluntary and involuntary spill to limit total dissolved gas.

JAMES R. MAHAR, P.E.

Operations Manager