### CENWP-OP-B                                                                                                                                  30 July 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 30 of 2006, which covers the period from 23 through 29 July 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 153.2 to 193.9 kcfs.  Daily average project tailwater elevation ranged from 13.7’ to 16.3’ msl.  Daily average powerhouse forebay elevation ranged from 75.5’ to 75.8 msl.  Daily average river temperature ranged between 71 and 73F.  Secchi disk measurements averaged 4.5 to 6.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 74.4 to 87.8 kcfs.

  - Unit Operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 had a 1% violation on 25 July due to STS inspections.

    - Unit 12 was out of service from 1032 on 28 July until 1442 on 29 July due to an emergency shutdown.

    - Unit 13 was out of service from 0500 on 24 July until 1326 on 26 July for governor repairs.  Unit 13 was operated out of FPP priority from 1106 until 1430 on 27 July for AVR adjustment testing.

    - Unit 14 had a 1% violation on 26 July due to STS inspections.  Unit 14 was operated out of FPP priority from 1106 until 1430 on 27 July for AVR adjustment testing.

    - Unit 16 was out of service from 0500 on 24 July until 1200 on 26 July for annual maintenance.  Unit 16 had a 1% violation on 26 July due to STS inspections.  Unit 16 went out of service at 1442 on 29 July for transformer maintenance.

    - Unit 18 had a 1% violation on 27 July due to STS inspections.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed.

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 7/25 | 623 |  |
| 12 | 7/25 | 465 |  |
| 13 | 7/25 | 396 | B and C rips repaired on 26 July |
| 14 | 7/26 | 422 |  |
| 15 | 7/26 | 549 |  |
| 16 | 7/26 | 230 |  |
| 17 | 7/27 | 457 |  |
| 18 | 7/27 | 611 | A missing rivets. Will repair on 31 July |

Table 1.  STS and VBS video inspections.

  - Dewatering and Fish Salvage.  No dewatering activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampling adult fish in the AFF.  One day restriction due to temperatures reaching 72F

  - CTUIR.  Currently at 549 out of 560 fish for Umatilla Basin re-introductions.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries- Gilbreath.  Salt water rearing subyearling chinook at the SMF continues.

  - NOAA Fisheries- McComas.  Acoustic tagging in the SMF continues.

  - NOAA Fisheries lamprey.  Sampling on hold due to water temperatures.

  - PSMFC smolt monitoring.  Adopted FPAC sampling protocols when water temps reached 70ºF.  Target sample size was reduced to 100 fish per day and processing every two hours throughout the day. The system went to bypass from 0700 on 25 July until 0700 on 26 July due to water temps reaching 72ºF.  The full-flow PIT tag detector became operational this week enabling PIT tag detection during full bypass.  12 subyearling chinook were collected for NOAA researchers.

  - PSMFC PIT tag.  Monthly testing of the B2CC detectors June through October.

  - PSMFC/USDA.  Pikeminnow angling from the project and in the tailrace BRZ.

  - U of I lamprey.  Testing concluded on 23 July.

  - WDFW Fish Counting.  Visual fish counting continues.

- FISHWAYS

  - Project biologists inspected 23 through 27 and 29 July 2006.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| All week | DSM2 airburst | Five screens not working. | Electrical | See 6.2.3 | 06-40863 |
| 7/23 | PH2 FB | TIES in unit 14 | Moved for barge access | TIES removed on 24 July. |  |
| 7/25-29 | Weir 38 | Reading <1.3’> | Unknown | Valve 2 opened more on 7/29 |  |
| 7/25 | Weir 37 | Reading <1.3’> | Unknown | Screen cleaned. |  |
| 7/29 | UMT weir | Reading <1.3’> | Unknown | No action taken |  |

Table 2.  FPP Out of Criteria items.

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

    - Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.

  - Fish Ladder Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | WS avg. | BI avg. | AFF max | SMF max |
| --- | --- | --- | --- | --- |
| 7/23 | 72.0 | 72.1 | 72.1 | 71.2 |
| 7/24 | 72.7 | 72.5 | 72.7 | 71.8 |
| 7/25 | 72.7 | 72.6 | 72.7 | 71.8 |
| 7/26 | 72.3 | 72.2 | 72.3 | 71.5 |
| 7/27 | 72.3 | 72.2 | 72.3 | 71.5 |
| 7/28 | 72.0 | 71.9 | 72.0 | 71.1 |
| 7/29 | 71.6 | 71.3 | 71.6 | 70.7 |

Table 3.  Bonneville Fishway temperatures

  - Sensor Calibration.  Calibration was checked on 29 July.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Comment period is open for two weeks.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23 PH1 STSs/VBSs will be scrapped.

  - SMF Full flow PIT Tag Detectors.  Testing ongoing.

- FISHWAY STATUS

  - Adult Fishways.

    - Cascades Island PLC is in manual.

    - Due to temperatures at the AFF reaching 72F, trapping is limited to one day a week.

  - Juvenile Fishways.

    - DSM1 remains out of service until 15 September.

    - The last of the TIES were removed on 24 July.

    - DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  The Project is waiting on contractors before repairs may be completed.

    - Due to temperatures at the SMF reaching 70F or greater, personnel will process fish more often to reduce holding time.   Temperatures reached 72F on 24 July.  Personnel switched the upper switchgate to bypass from 0700 on 25 July until 0700 on 26 July.

- HAZMAT, SPILLS AND CLEANUP - Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype sent on 28 June requests that Bonneville start summer spill at or above 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.

  - A teletype sent on 26 July requests a soft forebay constraint of 75.0’ – 76.5’ from 0600 until 1800 everyday from 31 July through 05 August.  This operation is necessary for SDS Lumber to maneuver a barge for rock placement.  Additional teletypes will be issued, as needed, until the work is completed in late August.

  - A 27 July teletype requests Bonneville tailwater remain below 16.0’ as a hard constraint from 0700 until 1200 on 28 July.  This is to facilitate the retrieval of sensors at Ives Island and Multnomah Falls by divers.

JAMES R. MAHAR, P.E.

Operations Manager