### CENWP-OP-B                                                                                                                          24 September, 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 38 of 2006, which covers the period from 17 through 23 September 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 82.0 to 126.6 kcfs.  Daily average project tailwater elevation ranged from 7.5’ to 11.3’ msl.  Daily average powerhouse forebay elevation ranged from 75.8’ to 76.4’ msl.  Daily average river temperature ranged between 65 and 67F.  Secchi disk measurements averaged 6.0 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.0 to 1.5 kcfs.

  - Unit Operation.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 was out of service from 0514 on 18 September until 1710 on 21 September due to the T-11 outage.

    - Unit 12 was out of service from 0406 on 18 September until 0115 on 22 September due to the T-11 outage.

    - Unit 13 remains out of service for a four year overhaul.

    - Unit 14 was out of service from 0406 on 18 September until 0806 on 22 September due to the T-11 outage.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F2 was in standby from 1527 on 18 September until 0723 on 20 September due to low tailwater elevations.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed.

    - FV6-9 was closed from 1250 until 1502 on 21 September due to an oil sheen resulting from truck salvage operations.  Please see 6.1

    - FV4-3 and FV4-4 were closed from 1030 until 1133 on 22 September to facilitate the removal of the sunken truck.  Please see 6.2

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

Table 1.  STS and VBS inspections.

  - Dewatering and Fish Salvage.  The following dewatering activities occurred this reporting week.

    - Three to five dozen crawfish were rescued from the salvaged truck.  See 6.2

- RESEARCH

  - CRITFC.  Sampling adult fish in the AFF.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries- Gilbreath.  SbyC collections concluded on 22 September.   Fish will continue to be held.

  - NOAA Fisheries- Jacobson.   Subyearling chinook collections concluded.

  - PSMFC smolt monitoring.  One fallback observed this week.  85 juvenile shad collected for UI.

  - University of Idaho.  Collecting juvenile shad from the SMF to understand their migration biology.  85 juvenile shad received from PSMFC.

  - USGS lamprey.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual fish counting continues.

  - WDFW and ODFW.  Tule counting will continue from 0700 until 1600 through the end of September.

- FISHWAYS

  - Project biologists inspected 17 through 23 September 2006.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| 9/17, 9/22 | B-branch So gate | Incorrect position for TW elev | System in manual | Operators adjusted. |  |
| 9/17, 9/22 | CI North gate | Incorrect position for TW elev | System in manual | Operators adjusted. |  |
| 9/19, 9/22 | B-branch diff. | Less than 1.0’ | System in manual | Operators adjusted |  |
| 9/19, 9/21 | Cascades Is. diff. | Less than 1.0’ | System in manual | Operators adjusted |  |
| 9/20, 9/22 | Weir 37 | Reading <1.0’> | Unknown | Operators adjusted |  |
| 9/20 | Weir 38 | Reading <1.0’> | Unknown | Operators adjusted |  |
| 9/21 | WS fishway | Exit and FV6-9 closed | Truck salvage | See 6.1 |  |
| 9/22 | B-Branch | FV4-3/FV4-4 closed | Truck Removal | See 6.2 |  |
| 9/22 | B-Branch | FG3-27 closed | System in manual | Operators opened |  |

Table 2.  FPP Out of Criteria items.

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH2 electronic velocity meter was incorrectly installed in the winter of 04/05.

    - Cascades Island FG6-12 is closed due to a bent shaft.  Repairs can not be made until winter 06/07.  this diffuser is out of criteria when tailwater exceeds 13’

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.  For now, the collection channel is operating within FPP criteria.

    - DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.

    - DSM2 orifice F2 B-S has separated from the shaft.  The orifice is ready for welding.  TR# 06-50979.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | WS avg. | BI avg. | AFF max | SMF max |
| --- | --- | --- | --- | --- |
| 9/17 |  | 67.0 | 67.2 | 66.4 |
| 9/18 |  | 67.0 | 67.1 | 66.4 |
| 9/19 |  | 66.6 | 66.7 | 66.0 |
| 9/20 |  | 66.3 | 66.4 | 65.7 |
| 9/21 |  | 65.6 | 65.5 | 65.0 |
| 9/22 |  | 65.0 | 65.1 | 64.5 |
| 9/23 |  | 65.4 | 65.5 | 64.8 |

Table 3.  Bonneville Fishway temperatures.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.

    - Cascades Island and B-Branch PLCs are in manual.

    - Stab plates remain installed in the PH2 FOGs.

  - Juvenile Fishways.

    - DSM1 will continue to remain OOS until removal in winter 07/08.

    - DSM2 orifice F2 B-S has separated from the shaft.  The orifice is in local and closed.  F2 B-N is open to compensate.

    - DSM2 orifice 14 A-S has separated from the shaft.  The orifice is closed in manual.

    - On 22 September, EC Electric did some work in the SMF headbox.  This required the upper switchgate power to be cut.  The switchgate power and air were tagged out from 0854 until 0926.  Due to the flushing water not being cleared out, water levels were a little higher than normal at the PDS.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Unit 11 will go OOS in early Oct, followed by units 15 and 16.

- HAZMAT, SPILLS AND CLEANUP –

  - On 04 May, a truck entered the Columbia, upstream of Bonneville, on the Washington Shore.  On 21 September, divers located the truck.  An oil sheen was later seen on the water moving towards the Washington Shore fish exit.  To prevent oil from entering the fishway, the exit and FV6-9 were closed from 1250 until 1502.  Oil absorbents were in place to try to recapture as much of the sheen as possible.

  - On 22 September, Navy divers and Corps personnel pulled the truck from the river.  Removal occurred at the south end of the Main Dam.  FV4-3 and FV4-4 were closed prior to the truck being towed to the vicinity in anticipation of the possibility of residual oil leaking when the truck was lifted from the water.  A sheen appeared on the water when the truck was lifted out.  Oil absorbents were placed at the entrances for FV4-3 and FV4-4 to recapture as much of the sheen as possible and to keep it out of the fishway.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype sent on 28 June requests that Bonneville start summer spill at or above 75 KCFS during daytime hours and spill to the 120% gas cap at night until further notice.

  - A teletype sent on 21 September modifies the dates requested for Bonneville pool be operated with a hard constraint 75.0 -76.5 feet, soft constraint 75.5 – 76.5 feet to reduce wear and tear on tribal nets.

0600 on 18 SEP – 1800 on 22 SEP

0600 on 25 SEP – 1800 on 29 SEP

JAMES R. MAHAR, P.E.

Operations Manager