### CENWP-OP-B                                                                                                                          01 October, 2006

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 39 of 2006, which covers the period from 24 through 30 September 2006.

- OPERATION SUMMARY

  - Daily average river flows ranged from 78.5 to 114.7 kcfs.  Daily average project tailwater elevation ranged from 7.5’ to 10.5’ msl.  Daily average powerhouse forebay elevation ranged from 76.0’ to 76.4’ msl.  Daily average river temperature ranged between 65 and 66F.  Secchi disk measurements averaged 6.5 to 7.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 1.3 to 1.4 kcfs.

  - Unit Operation.  GDACS testing occurred on all units on 26 September.

    - Unit 0 remains out of service due to governor trouble.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 had a 1% violation on 26 September due to STS inspections and on 27 September for trashrack raking.  Unit 11 was out of service from 1036 until 1156 on 29 September to facilitate the delivery of the spare STS.

    - Unit 12 was out of service from 1036 until 1156 on 29 September to facilitate the delivery of the spare STS.

    - Unit 13 remains out of service for a four year overhaul.

    - Unit 14 was out of service from 0700 until 1114 on 26 September for exciter repair.

    - Unit 15 was out of service from 0646 until 0910 on 28 September for STS repairs.

    - Unit 16 had a 1% violation on 27 September due to STS inspections.

    - Unit 18 had a 1% violation on 27 September due to STS inspections.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Only one fish unit is operating at a time due to low tailwater elevations.  Washington Shore fishway remains in FPP criteria.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed.

    - FV1-1 was closed for cleaning from 1520 until 1544 on 25 September.

  - STS/VBS Inspections.  The following STSs/VBSs were inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 9/26 | 586 |  |
| 12 | 9/26 | 543 |  |
| 13 |  | 0 | Out of service |
| 14 | 9/27 | 345 |  |
| 15 | 9/27 | 645 | Repaired rivets |
| 16 | 9/27 | 314 |  |
| 17 | 9/27 | 615 |  |
| 18 | 9/27 | 471 |  |

Table 1.  STS and VBS inspections.

  - Dewatering and Fish Salvage.  No dewatering activities occurred this reporting week.

- RESEARCH

  - CRITFC.  Sampling adult fish in the AFF.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - NOAA Fisheries- Gilbreath.  Fish continue to be held.

  - PSMFC smolt monitoring.  One fallback observed this week.  50 juvenile shad collected for UI.

  - University of Idaho.  Collecting juvenile shad from the SMF to understand their migration biology.  50 juvenile shad received from PSMFC.

  - USGS lamprey.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual fish counting continues.

  - WDFW and ODFW.  Tule counting concluded.

- FISHWAYS

  - Project biologists inspected 24 through 30 September 2006.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| 9/24 | B-branch South gate | Incorrect position for TW elev | System in manual | Operators adjusted. |  |
| 9/24 | B-Branch | FG3-27 open | System in manual | Operators adjusted |  |
| 9/25 | B-Branch diff. | Reading <1.0’> | System in manual | Operators adjusted |  |
| 9/30 | B-Branch weir | Reading <1.0> | Unknown | No action taken |  |
| 9/24 | Cascades Is. North gate | Incorrect position for TW elev | System in manual | Operators adjusted. |  |
| 9/24 | Cascades Is. | FG6-14 open | System in manual | Operators adjusted |  |
| 9/25 | Cascades Is. diff | Reading <1.0’> | System in manual | Operators adjusted |  |
| 9/27-28 | Weirs 37/38 | Reading <1.0> | Unknown | No action taken |  |
| 9/30 | Bay 18 | Closed | Working on controls | Closed <10 minutes. |  |

Table 2.  FPP Out of Criteria items.

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH2 electronic velocity meter was incorrectly installed.  Will be corrected this winter.

    - Cascades Island FG6-12 is closed due to a bent shaft.  This is OOC when TW exceeds 13’.  Repairs will be made this winter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Diffuser failure occurred during water up.  Repairs are scheduled for winter 07/08.

    - DSM2 airburst screens 1, 4, 5, 11 and 12 do not operate consistently.  A portion of the PLC has been reprogrammed.  TR#06-40863.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   WS temps were missing from last week’s report, so they have been included this week.

| Date | WS avg. | BI avg. | AFF max | SMF max |
| --- | --- | --- | --- | --- |
| 9/17 | 67.2 | 67.0 | 67.2 | 66.4 |
| 9/18 | 67.2 | 67.0 | 67.1 | 66.4 |
| 9/19 | 66.8 | 66.6 | 66.7 | 66.0 |
| 9/20 | 66.4 | 66.3 | 66.4 | 65.7 |
| 9/21 | 65.7 | 65.6 | 65.5 | 65.0 |
| 9/22 | 65.2 | 65.0 | 65.1 | 64.5 |
| 9/23 | 65.6 | 65.4 | 65.5 | 64.8 |
| 9/24 | 65.2 | 64.9 | 65.1 | 64.3 |
| 9/25 | 65.0 | 64.8 | 65.0 | 64.1 |
| 9/26 | 65.1 | 65.0 | 65.1 | 64.2 |
| 9/27 | 65.8 | 65.3 | 65.8 | 64.9 |
| 9/28 | 66.3 | 66.1 | 66.3 | 65.5 |
| 9/29 | 66.5 | 66.4 | 66.5 | 65.7 |
| 9/30 | 66.4 | 66.2 | 66.3 | 65.6 |

Table 3.  Bonneville Fishway temperatures.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration is checked on the weekends.  Cascades Island entrance is significantly out of calibration.

    - Cascades Island and B-Branch PLCs are in manual.

    - Stab plates remain installed in the PH2 FOGs.

  - Juvenile Fishways.

    - DSM1 will continue to remain OOS until removal in winter 07/08.

    - DSM2 orifice F2 B-S was repaired and back in auto on 25 September.

    - DSM2 orifice 14 A-S was repaired and back in auto on 25 September.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Unit 16 will go OOS in early Oct, followed by units 11 and 15.

- HAZMAT, SPILLS AND CLEANUP – nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS.

  - A teletype sent on 21 September modifies the dates requested for Bonneville pool be operated with a hard constraint 75.0 -76.5 feet, soft constraint 75.5 – 76.5 feet to reduce wear and tear on tribal nets.

0600 on 25 SEP – 1800 on 29 SEP

0600 on 03 OCT – 1800 on 06 OCT

  - On 05 October, the Cascades Island exit, picket leads, and lamprey barrier will be opened.  The north UMT bulkhead will be installed.  Fish will be allowed to exit the UMT until the south bulkhead is installed on 10 October.  Fish salvage activities will occur on 10 October.

  - Bonneville’s winter maintenance schedule is available.  Please contact Fisheries for a copy.

JAMES R. MAHAR, P.E.

Operations Manager