### CENWP-OP-B                                                                                                                          08 January, 2007

MEMORANDUM FOR CENWP-OP, ATTN: Randy Bailey

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 01 of 2007, which covers the period from 31 December 2006 through 06 January 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 129.9 to 190.5 kcfs.  Daily average project tailwater elevation ranged from 13.2’ to 18.0’ msl.  Daily average powerhouse forebay elevation ranged from 74.0’ to 75.6’ msl.  Daily average river temperature ranged from 41F to 42F.  Secchi disk measurements averaged 2.5 to 6.0 feet.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 0.5 to 9.6 kcfs.

    - Spill Bay 1 remains closed during all hours.

    - Spill Bay 18 is open during daylight hours.

  - Unit Operation.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 3 was out of service from 1354 until 1939 on 04 January and from 1406 until 1900 on 05 January for Bank 3/4 work.

    - Unit 4 was out of service from 1354 on 04 January until 1900 on 05 January for Bank 3/4 work.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 11 remains out of service for VBS mods.

    - Unit 13 remains out of service for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are currently out of service for winter maintenance.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed.

    - FV1-1 closed for cleaning from 0850 until 0920 on 03 January.

    - FV5-3, FV5-4, and FV5-9 remain closed for winter maintenance in the Cascades Island fishway.

    - FV6-9 remains closed for winter maintenance in the Washington Shore fishway.

  - STS/VBS Inspections.  STSs/VBSs have been removed for winter maintenance.  Screens will be installed the last week of February.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | All screens removed for winter maintenance. |

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - USGS lamprey.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Video counting continues at Bradford Island.

- FISHWAYS

  - Project biologists inspected on 31 December 2006 and 3-4 January 2007.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 12/31 | B-Branch | FG3-24 open | System in manual | Operators closed. |  |
| 1/4 | B-Branch | FG3-23 closed | System in manual | Operators opened. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration is checked on the weekends.  B-branch tailwater is out of calibration.

    - B-Branch PLC is in manual.

    - WS and CI remain dewatered.

  - Juvenile Fishways.

    - DSM1 will continue to remain OOS until removal in winter 07/08.

    - DSM2 remains dewatered.

  - Lamprey Fishways.  Remains dewatered.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 32 PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Unit 16 is complete.  Unit 11 is OOS.  Unit 15 will be next.

- HAZMAT, SPILLS AND CLEANUP – nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.

JAMES R. MAHAR, P.E.

Operations Manager