### CENWP-OP-B                                                                                                                          20 February 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 07 of 2007, which covers the period from 11 February through 17 February 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 146.6 to 162.9 kcfs.  Daily average project tailwater elevation ranged from 13.1’ to 15.3’ msl.  Daily average powerhouse forebay elevation ranged from 72.8’ to 76.0’ msl.  Daily average river temperature ranged between 38F and 40F.  Secchi disk measurements averaged 6.0’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill averaged 0.5 to 0.6 kcfs.

    - Spill Bay 1 remains closed during all hours.

    - Spill Bay 18 is open during daylight hours.

  - Unit Operation.  First Powerhouse priority.

    - Unit 2 remains out of service for turbine rehab.

    - Unit 5 was out of service from 1936 until 2033 on 16 February due to governor lockup.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.

    - Unit 13 remains out of service for a four year overhaul.

    - Unit 15 went out of service at 1243 on 08 February to facilitate VBS/gatewell modifications.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are currently out of service for winter maintenance.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves are closed.

    - FV1-1 was closed from 1545 until 1600 on 15 February for cleaning.

    - FV5-3, FV5-4, and FV5-9 remain closed for winter maintenance in the Cascades Island fishway.

    - FV6-9 remains closed for winter maintenance in the Washington Shore fishway.

  - STS/VBS Inspections.  STSs/VBSs have been removed for winter maintenance.  Screens will be installed the last week of February.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | All screens removed for winter maintenance. |

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this week.

- RESEARCH

  - Battelle.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.

  - ERDC TDG.  Sensors remain installed in the tailrace.

  - Fish Field Unit.  Pinniped observations continue.

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - USGS.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Video counting continues at Bradford Island.

- FISHWAYS

  - Project biologists inspected 15 through 16 February 2007.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 2/15 | Bradford Is. | BI weir < 1.0 | FV 3-9 not controlling properly. | TR | 07-15505 |
| 2/15 | A-Branch | Weir < 1.0 | FV 3-9 not controlling properly. | TR | 07-15505 |
| 2/15 | B-Branch | Weir < 1.0 | FV 3-9 not controlling properly. | TR | 07-15505 |
| 2/17 | Bonneville Dam | Less than 3 inspections per week | Illness |  |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

  - Fishway Temperatures.  Temperatures are taken 01 March through 30 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration is checked on the weekends.  B-branch tailwater is out of calibration.

    - B-Branch PLC is in manual.

    - WS and CI remain dewatered.

    - SLEDS are installed at PH1, PH2, and B-branch fishway entrances.

  - Juvenile Fishways.

    - DSM1 will continue to remain OOS until removal in winter 07/08.

    - DSM2 returned to service at 1200 on 16 February and is in bypass.

  - Lamprey Fishways.  Remains dewatered.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 24 PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Units 11 and 16 are complete.  Unit 15 is currently OOS.

- HAZMAT, SPILLS AND CLEANUP – nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.

  - A teletype sent on 12 February requests that forebay elevation be kept as low as possible, preferably below 73 feet, as a soft constraint, during the hours of 0700 – 1800 Tuesday, 13 February.  Lower pool elevations will continue to assist debris removal efforts in Rock Creek.

  - A teletype sent on 14 February outlines operations necessary for the project to complete a spillway operation/calibration test as part of a regular maintenance regime.  During hours of 0700 – 1500, Monday, 19 February, open one spillbay at a time as much as one foot.  Maximum instantaneous spill levels on tested bays will be 2.3 kcfs with an average spill of 1.5 kcfs through the period (in addition to normal spillbay 18 spill).  Spillbay 18 will remain open (normal operations per the Fish Passage Plan) while other bays are tested.

JAMES R. MAHAR, P.E.

Operations Manager