### CENWP-OP-B                                                                                                                          23 April 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 16 of 2007, which covers the period from 15 through 21 April 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 211.5 to 255.7 kcfs.  Daily average project tailwater elevation ranged from 17.7’ to 19.9’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 75.4’ msl.  Daily average river temperature ranged between 48F and 50F.  Secchi disk measurements averaged 4.2’ to 6.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are open 0.5’ during daylight hours and are included in the spill pattern.  Daily average spill averaged 97.7 to 100.9 kcfs.

  - Unit Operation. Powerhouse 2 priority.

    - Unit 1 was out of service from 0526 until 1224 on 18 April for slip ring maintenance.

    - Unit 5 was out of service from 0730 until 1700 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 6 was out of service from 0730 until 1700 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 7 was out of service from 0730 until 1700 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 remains out of service for turbine rehab.  U10 started the 72 hour heat run at 1655 on 18 April.

    - Unit 11 was out of service from 0730 until 1702 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 12 was out of service from 0730 until 1702 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 13 was out of service from 0730 until 1708 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 14 was out of service from 0730 until 1703 on 16 April to facilitate N. Bonneville substation maintenance by BPA.  U14 was OOS from 0659 until 0855 on 19 April for STS work.

    - Unit 15 remains out of service due to headgate problems.

    - Unit 16 was out of service from 0730 until 1708 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Unit 17 returned to service at 1721 on 16 April.

    - Unit 18 was out of service from 0730 until 1658 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - Fish Unit 1 was out of service from 0420 until 2140 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

    - Fish Unit 2 was out of service from 0439 until 2142 on 16 April to facilitate N. Bonneville substation maintenance by BPA.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed for cleaning.

    - FV1-1 was closed from 0727 until 0920 on 19 April.

  - STS/VBS Inspections.  STSs/VBSs inspections are scheduled for the week of 22 April.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.

  - Battelle.  Installed/ing equipment in the spillway for a spillway survival evaluation.

  - Fish Field Unit.  Sea lion observations continue.

  - Hatchery releases.  Spring Creek NFH released 4.2 million tule chinook and Carson and Little White Salmon NFH released 2.16 million yearling chinook on 12 April  As anticipated, these fish started showing up at the JMF on 13 April.  See 4.6.4

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - PSMFC Smolt Monitoring.  One adult steelhead crossed the separator bars.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Hazing sea lions from the powerhouses continues.

  - USGS.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 15-21 April 2007.   NOAA Fisheries and USFWS inspected on 20 April.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 4/18 | BI weir | Reading <1.0’ | FV3-9 not controlling properly | Operators adjusted FV3-9 |  |  |
| 4/20 | FV3-7 | Open more than needed. | Valve in auto w/2 available diffusers | Valve returned to manual. See 4.5.3 |  |  |
| 4/16, 4/18 | A-Branch weir | Reading <1.0’> | FV3-9 not controlling properly | FV3-9 adjusted |  |  |
| 4/18-19 | PH1 PCC south end | Differential <1.0’ | FV1-1 not controlling properly | Operators adjusted FV1-1 |  |  |
| 4/18 | B-Branch weir | Reading <1.0’> | FV3-9 not controlling properly | FV3-9 adjusted |  |  |
| 4/16 | FG3-24 | Incorrect position | Unknown | Operators corrected |  |  |
| 4/19 | B-Branch N. ent. gate | Closed | Unknown | Operators notified |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| 4/20 | FG6-9 | Open | To compensate for FG6-10 |  |  |  |
| 4/20 | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted |  |  |
| 4/16 | FG6-11 | Open | TW reading high | Operators corrected |  |  |
| 4/18-21 | FG6-14 | ½ way open | Electricians working on the power supply | Electricians working on the wiring. |  |  |
| 4/16 | S. ent. gate | Closed | Gate is in manual | Operators notified |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| 4/16 | WS fishway | Entire system down | BPA maintenance | Back in service by 1700. |  |  |
| 4/18-19 | Weir 37 | Reading <1.0’> | In manual |  |  |  |
| 15,17,19 | Weir 38 | Reading <1.0’> | Unknown | Valve #2 adjusted. |  |  |
| 4/16, 4/20-21 | Velocity meter | Reading <1.5 fps | Unknown, works intermittently. |  |  |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 4/15 | 49.2 | 49.2 |
| 4/16 | 49.6 | 49.6 |
| 4/17 | 49.5 | 19.3 |
| 4/18 | 49.8 | 49.8 |
| 4/19 | 50.1 | 50.2 |
| 4/20 | 50.3 | 50.3 |
| 4/21 | 50.5 | 50.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends again, when the new bio starts on 14 May.

    - B-Branch and Cascades Island PLCs are in automatic.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - SLEDS installed at all main fish entrances.

    - Stab plates remain installed in the FOGs due to the sea lion barriers not fitting properly.

    - Sea lion C404 has been spotted in the Washington shore fishway, beyond the count window.  He is climbing over the floating orifice gates.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B were opened to 71.5’ from 17 April until 19 April.  The gates were opened as per FPOM agreement.  They had to be closed due to some trashraking activities going on at U10 and the inability of the new gantry crane to reach those gates while the old crane is in place.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights continue to be lighted with the halogen bulbs.

    - On 13 April, smolt monitoring personnel reported increased mortality in Spring Creek fish.  Please see the 070416 Memo For the Record distributed by Bonneville Project Fisheries.  If you would like a copy, please contact Tammy Mackey at 541-374-4552.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service as of 23 March.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  All units are complete.  Units 14 and 18 are scheduled for winter 07/08.

- HAZMAT, SPILLS AND CLEANUP –nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 13 April requests that available units be run outside the 1% efficiency range from 0500 until 1700 on 16 April.  This operation will coincide with the scheduled powerhouse transmission line outage scheduled for 0700 until 1700 on 16 April.  This operation will also precede spilling in excess of the gas cap.

  - A teletype sent on 13 April requests a change in powerhouse priority and operation to reduce impacts to juvenile fish passing through the juvenile monitoring facility.  Effective immediately, the project is to operate as follows, while spilling 100 kcfs:

    - Operate Units 14 and 18 within the 1% efficiency

    - Operate available units (11-13, and 16-17) at the low end of 1%.

    - Operate available PH1 units within the 1% efficiency.

    - Spill to the gas cap.

    - Operate PH1 units outside the 1% efficiency to meet flow requirements.

  - A teletype sent on 15 April approves an exceedance of the 24 hour tailwater fluctuation limit of 4’.  This is effective 0001 through 2359 on 16 April.  This tailwater exceedance is needed to reduce spill during the 16 April transmission line outage (see7.3).

JAMES R. MAHAR, P.E.

Operations Manager