### CENWP-OP-B                                                                                                                          30 April 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 17 of 2007, which covers the period from 22 through 28 April 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 209.3 to 242.8 kcfs.  Daily average project tailwater elevation ranged from 17.5’ to 19.2’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 75.4’ msl.  Daily average river temperature ranged between 50F and 52F.  Secchi disk measurements averaged 4.5’ to 6.5’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 97.4 to 99.5 kcfs.

  - Unit Operation. PH 2 priority.  Units 11-18 had 1% violations for STS inspections on 25 April.

    - Unit 1 was out of service from 0526 until 1224 on 18 April for slip ring maintenance.

    - Unit 7 was out of service from 0550 on 23 April until1640 on 24 April for pre rehab inspections.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 9 was out of service from 0700 until 1710 on 24 April for annual maintenance.

    - Unit 10 returned to service at 1047 on 26 April.

    - Unit 11 was out of service from 0637 until 1600 on 26 April for STS repair.   As of 25 April, Unit 11 will be operated at the lower end of 1% (whenever possible) to help reduce debris loads.

    - Unit 15 remains out of service due to STS screen problems.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed.

    - FV5-3 and FV5-4 were closed down from 1415 until 1645 on 25 April to allow Battelle into the spillway for equipment installation.

  - STS/VBS Inspections.  STSs/VBSs inspections are scheduled for the week of 22 April.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 4/25 | 682 | A and B screens were ripped. |
| 12 | 4/25 | 683 |  |
| 13 | 4/25 | 538 |  |
| 14 | 4/25 | 680 |  |
| 15 |  |  | OOS |
| 16 | 4/25 | 665 |  |
| 17 | 4/25 | 552 |  |
| 18 | 4/25 | 687 |  |

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities occurred this reporting week.

- RESEARCH

  - Battelle.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.

  - Battelle.  Installed equipment in the spillway for a spillway survival evaluation.

  - Fish Field Unit.  Sea lion observations continue.

  - Hatchery releases.  Spring Creek NFH is expected to release tule chinook the week of 29 April.

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - PSMFC Smolt Monitoring.  Eight adult steelhead crossed the separator bars.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Hazing sea lions from the powerhouses continues.

  - USGS.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 22-28 April 2007.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 4/22-23, 4/25 | BI weir | Reading <1.0’ | FV3-9 not controlling properly | Operators adjusted FV3-9 |  |  |
| 4/23, 4/25 | A-Branch weir | Reading <1.0’> | FV3-9 not controlling properly | FV3-9 adjusted |  |  |
| 4/25 | PH1 PCC south end | Differential <1.0’ | FV1-1 not controlling properly | Operators adjusted FV1-1 |  |  |
| 4/23, 4/25 | B-Branch weir | Reading <1.0’> | FV3-9 not controlling properly | FV3-9 adjusted |  |  |
| 4/23, 4/26 | FG3-23 | Incorrect position | Unknown | Operators corrected |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| See 4.2.6 | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted |  | 07-37350 |
| All week | FG6-14 | ½ way open | Electricians working on the power supply | Electricians working on the wiring. |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| 4/22-23 | SA24 Board | SUE readout blank | Unknown | TR submitted |  | 07-36771 |
| 4/23 | Weir 37 | Reading <1.0’> | In manual | Elec. working on it |  |  |
| 4/22 | Weir 38 | Reading <1.0’> | Unknown | Valve #2 adjusted. |  |  |
| 4/22-23, 4/25 | Velocity meter | Reading <1.5 fps | Sometimes needs to be reset. | Elec. and Fish will monitor. |  |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Mechanics will make repairs as soon as they finish with work on U2.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 4/22 | 50.8 | 50.7 |
| 4/23 | 51.1 | 51.1 |
| 4/24 | 51.4 | 51.4 |
| 4/25 | 51.5 | 51.5 |
| 4/26 | 51.7 | 51.6 |
| 4/27 | 52.3 | 52.3 |
| 4/28 | 52.7 | 52.7 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends again, when the new bio starts on 14 May.

    - B-Branch and Cascades Island PLCs are in automatic.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - SLEDS installed at all main fish entrances.

    - Stab plates remain installed in the FOGs due to the sea lion barriers not fitting properly.

    - Weir 37 had a new electronics installed on 23 April.  The valve is controlling properly now.

    - FV4-4 has, periodically, been in manual to facilitate break repair from 23 until 25 April.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights continue to be lighted with the halogen bulbs.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service as of 23 March.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  All units are complete.  Units 14 and 18 are scheduled for winter 07/08.

- HAZMAT, SPILLS AND CLEANUP –nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 24 April requests a 100Kcfs hard constraint on spill from 0800 until 1800 from 24-25 April.  This will allow Battelle to safely deploy hydrophones in the spillway forebay.

  - A teletype sent on 30 April requests a change in powerhouse priority and operation to reduce impacts to juvenile fish passing through the juvenile monitoring facility.  Effective 0001 on 02 May until 2359 on 04 May, the Project is to operate as follows, while spilling 100Kcfs:

    - Operate Units 14 and 18 within the 1% efficiency

    - Operate available units (11-13, and 16-17) at the low end of 1%.

    - Operate available PH1 units within the 1% efficiency.

    - Operate PH1 units 3,1,4,6,2,5,7,10,9,8 within the 1% efficiency.

    - Increase units 17, 16, 15, 13, 12, 11, in this order up to full 1% one unit at a time.

JAMES R. MAHAR, P.E.

Operations Manager