### CENWP-OP-B                                                                                                                          07 May 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 18 of 2007, which covers the period from 29 April through 05 May 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 240.8 to 287.4 kcfs.  Daily average project tailwater elevation ranged from 19.1’ to 22.1’ msl.  Daily average powerhouse forebay elevation ranged from 73.9’ to 75.4’ msl.  Daily average river temperature ranged between 52F and 53F.  Secchi disk measurements averaged 4.’  to 5.5’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 92.7 to 95.9 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 2 was out of service for slip ring turning from 0300 on 30 April until 1408 on 3 May.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 15 remains out of service.  Its four year overhaul started on 01 May.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed.

    - FV1-1 was closed for cleaning from 1545 until 1604 on 3 May.

  - STS/VBS Inspections.  STSs/VBSs inspections are scheduled for May.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  Biologists removed two unclipped adult chinook and about 100 juvenile salmon and steelhead from the U15 draft tube on 02 May.  All fish were released safely.  The number of juveniles were a result of the gatewell dipping basket no longer fitting in the modified gatewell slots.  As a result, gatewell dipping was not done.

- RESEARCH

  - Battelle kelt passage.  Monitoring with hydroacoustics near B2CC entrance to study kelt passage.

  - Battelle spillway survival.  Installed equipment in the spillway for a spillway survival evaluation.

  - Fish Field Unit.  Sea lion observations continue.

  - Hatchery releases.  Spring Creek NFH released tule chinook the week of 29 April.

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - PSMFC Smolt Monitoring.  Eight adult steelhead and 1 adult salmon crossed the separator bars.   1209 clipped yearling chinook were collected for NOAA Fisheries and Battelle.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Hazing sea lions from the powerhouses continues.

  - USGS.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 29 April through 05 May.  NOAA Fisheries inspected on 04 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 5/2 | BI weir | Reading <1.0’ | FV3-9 not controlling properly | Operators adjusted FV3-9 |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. She starts on 14 May. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| 4/30-5/5 | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted. See 4.2.6 |  | 07-37350 |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| All week | Velocity meter | Not reading at all. | Improper wiring. | Electricians are working with the manufacturer. Should be operable by 11 May. |  | 07-36771 |
| 4/30-5/5 | 11A-S | Closed | Broken shaft | Mech. working on it. |  | 07-40917 |
| 5/1-5/5 | Weir 38 | Reading <1.0’> | Unknown | Valve #2 adjusted. |  |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Mechanics will make repairs as soon as they finish with work on U2.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 4/29 | 53.0 | 52.9 |
| 4/30 | 53.2 | 53.2 |
| 5/1 | 53.2 | 53.1 |
| 5/2 | 53.3 | 53.1 |
| 5/3 | 53.7 | 53.5 |
| 5/4 | 53.9 | 53.6 |
| 5/5 | 53.8 | 53.7 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends again, when the new bio starts on 14 May.

    - B-Branch and Cascades Island PLCs are in automatic.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - SLEDS installed at all main fish entrances.

    - Stab plates remain installed in the FOGs due to the sea lion barriers not fitting properly.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights continue to be lighted with the halogen bulbs.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service as of 23 March.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  All units are complete.  Units 14 and 18 are scheduled for winter 07/08.

- HAZMAT, SPILLS AND CLEANUP –nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 22 December details tailwater operations for chum incubation.   Effective as soon as possible, a hard tailwater constraint to operate project tailwater no lower than 13.0 feet during all hours.  One pulse per day with a minimum duration of 20 minutes and minimum elevation of 13.5 feet.

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 30 April requests a change in powerhouse priority and operation to reduce impacts to juvenile fish passing through the juvenile monitoring facility.  Effective 0001 on 02 May until 2359 on 04 May, the Project is to operate as follows, while spilling 100Kcfs:

    - Operate Units 14 and 18 within the 1% efficiency

    - Operate available units (11-13, and 16-17) at the low end of 1%.

    - Operate available PH1 units within the 1% efficiency.

    - Operate PH1 units 3,1,4,6,2,5,7,10,9,8 within the 1% efficiency.

    - Increase units 17, 16, 15, 13, 12, 11, in this order up to full 1% one unit at a time.

  - A teletype send on 04 May requests an extension of the modified unit operations, detailed in 7.3 above, until 0700 on 05 May.  The request was made in anticipation of 95% of the Spring Creek tule chinook passing the project by 0700 on 05 May.

JAMES R. MAHAR, P.E.

Operations Manager