### CENWP-OP-B                                                                                                                          21 May 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 20 of 2007, which covers the period from 13 through 19 May 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 257.5 to 301.0 kcfs.  Daily average project tailwater elevation ranged from 20.1’ to 22.1’ msl.  Daily average powerhouse forebay elevation ranged from 72.5’ to 75.1’ msl.  Daily average river temperature ranged between 55F and 57F.  Secchi disk measurements averaged 3.0’ to 5.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 97.7 to 99.0 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 was out of service from 2025 on 16 May until 0834 on 17 May due to exciter trouble.

    - Unit 11 was out of service from 0716 on 16 May until 1129 on 17 May for trashrack raking and inspection.

    - Unit 15 remains out of service.  Its four year overhaul started on 01 May.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this week:

2.1.1   FV 1-1 closed for cleaning from 1536 until 1556 on 17 May.

  - STS/VBS Inspections.  STSs/VBSs inspections are scheduled for the week of 20 May.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  No dewatering or salvage activities this week.

- RESEARCH

  - Battelle spillway survival.  Releasing juvenile yearling chinook in the spillway forebay for a spillway survival evaluation.

  - Fish Field Unit.  Sea lion observations continue.

  - NOAA.  Salt water rearing at the Smolt Monitoring Facility.

  - NOAA.  B2CC detection evaluation underway.

  - NOAA.  Tagging juvenile yearling chinook at the Smolt Monitoring Facility.

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - PSMFC Smolt Monitoring.  Four adult salmon and three steelhead crossed the separator bars.   2,566 clipped yearling chinook were collected for NOAA Fisheries and Battelle.

  - University of Idaho.  Spring chinook evaluations continue.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Hazing sea lions from the powerhouses continues.

  - USGS.  Lamprey held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 13 through 19 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 5/13-5-15 | A-branch | Staff gauge> 1.3 | Shad passage reprogramming | Electricians adjusted |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. She starts on 14 May. |  |  |
| 5/16 | Collection channel | Entrance differential < 1.0 | Weir gate 2 not controlling properly | Operator adjusted weir gate 2 |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. She starts on 14 May. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| All week | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted. See 4.2.6 |  | 07-37350 |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| All week | 11A-S | Closed | Broken shaft | Mech. working on it. |  | 07-40917 |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Mechanics will make repairs as soon as they finish with work on U2.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 5/13 | 55.6 | 55.3 |
| 5/14 | 55.9 | 55.7 |
| 5/15 | 56.6 | 56.5 |
| 5/16 | 57.4 | 57.2 |
| 5/17 | 57.6 | 57.4 |
| 5/18 | 57.8 | 57.6 |
| 5/19 | 58.1 | 57.9 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends.

    - B-Branch and Cascades Island PLCs are in automatic.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - SLEDS installed at all main fish entrances.

    - Stab plates remain installed in the FOGs due to the sea lion barriers not fitting properly.

    - Ladders placed in shad passage mode

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights continue to be lighted with the halogen bulbs.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service.

    - The NDE lamprey ramp is schedule to be lowered on 29 May.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  All units are complete.  Units 14 and 18 are scheduled for winter 07/08.

- HAZMAT, SPILLS AND CLEANUP  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 16 April requests that spillbay 18 be opened to flush trash from the forebay.  The spillbay should be opened for no more than 30 minutes and then returned to its normal spill pattern position.

JAMES R. MAHAR, P.E.

Operations Manager