### CENWP-OP-B                                                                                                                          28 May 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 21 of 2007, which covers the period from 20 through 26 May 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 253.6 to 272.7 kcfs.  Daily average project tailwater elevation ranged from 19.9’ to 20.8’ msl.  Daily average powerhouse forebay elevation ranged from 72.9’ to 75.1’ msl.  Daily average river temperature ranged between 57F and 59F.  Secchi disk measurements averaged 3.5’ to 5.8’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 95.6 to 99.0 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 8 remains out of service for turbine rehab.

    - Unit 10 was out of service from 0906 until 1056 on 24 May due to slip ring work.

    - Unit 14 had a 1% violation from 1049 until 1145 on 21 May for STS inspection.

    - Unit 15 remains out of service.  Its four year overhaul started on 01 May.

    - Unit 18 had a 1% violation from 1355 until 1533 on 21 May for STS inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this week:

  - STS/VBS Inspections.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 5/22 | 597 |  |
| 12 | 5/22 | 629 |  |
| 13 | 5/22 | 629 |  |
| 14 | 5/22 | 629 |  |
| 15 | NA |  | OOS |
| 16 | 5/22 | 608 |  |
| 17 | 5/22 | 636 |  |
| 18 | 5/22 | 637 |  |

  - Dewatering and Fish Salvage.  No dewatering or salvage activities this week.

- RESEARCH

  - Battelle spillway survival.  Releasing juvenile yearling chinook in the spillway forebay for a spillway survival evaluation.

  - Fish Field Unit.  Sea lion observations continue.

  - NOAA.  Salt water rearing at the Smolt Monitoring Facility.

  - NOAA.  B2CC detection evaluation underway.

  - NOAA.  Tagging juvenile yearling chinook at the Smolt Monitoring Facility.

  - NOAA Lamprey.  Construction of the lamprey ramp in the WA shore AWS began in mid January.

  - PSMFC Smolt Monitoring.  Four adult salmon and three steelhead crossed the separator bars.   2,566 clipped yearling chinook were collected for NOAA Fisheries and Battelle.

  - University of Idaho.  Spring chinook evaluations continue.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Hazing sea lions from the powerhouses continues.

  - USGS.  Lamprey continue to be held in the FERL for tagging evaluation.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

  - WDFW/ODFW/CRITFC Sea lion hazing.  Hazing from boats continues.

- FISHWAYS

  - Project biologists inspected on 20 through 26 May.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 5/26 | B-branch | Entrance differential > 1.5 | Unknown | Operator adjusted |  |  |
| Once | Calibration | Check not done | Short-handed | New bio hired. She started on 14 May. |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| All week | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted. See 4.2.6 |  | 07-37350 |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| All week | 11A-S | Closed | Broken shaft | Mech. working on it. |  | 07-40917 |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Mechanics will make repairs as soon as they finish with work on U2.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 5/20 | 58.1 | 57.9 |
| 5/21 | 57.7 | 57.5 |
| 5/22 | 57.8 | 57.6 |
| 5/23 | 58.0 | 57.8 |
| 5/24 | 58.3 | 58.2 |
| 5/25 | 58.5 | 58.4 |
| 5/26 | 59.0 | 58.8 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends.

    - B-Branch and Cascades Island PLCs are in automatic.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - SLEDS and floating orifice gate stab plates will be removed beginning the week of 27 May.

    - As of 10 May, the fish ladders are in shad passage mode.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights continue to be lighted with the halogen bulbs.

    - The ERG tripped on 23 May at 2332 for an unknown reason.  There was no visible debris but the initial attempts to reset the ERG were unsuccessful.  The add-in valve was closed to 50% and all south regulating orifices were closed to enable the system to be reset at 0125.  All components were returned to normal operating positions after the reset.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service.

    - The NDE lamprey ramp is schedule to be lowered on 29 May.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.

- HAZMAT, SPILLS AND CLEANUP  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 11 May requests the Project maintain a forebay soft constraint of 71.5’ to 72.5’ from 0900 until 1800 on 19-20 May.  This request is to allow a work party to stockpile debris on the kite board staging area, instead of leaving it strewn about the area.

  - A teletype sent on 21 May requests that the fish units be throttled back from 1300 until 1400 hours to allow the installation of the lamprey ramp at the Washington shore north downstream entrance.

  - A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.

  - A teletype sent on 25 May requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operate outside of the 1% best efficiency standard only under the declaration of a system emergency.

  - A teletype sent on 25 May requests that Bonneville project operate spillbay 1 as needed, but for no more than 30 minutes, to flush trash from the forebay.

JAMES R. MAHAR, P.E.

Operations Manager