### CENWP-OP-B                                                                                                                          11 June 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 23 of 2007, which covers the period from 03 through 09 June 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 223.4 to 282.6 kcfs.  Daily average project tailwater elevation ranged from 18.0’ to 21.2’ msl.  Daily average powerhouse forebay elevation ranged from 74.2’ to 75.3’ msl.  Daily average river temperature ranged between 61F and 62F.  Secchi disk measurements averaged 4’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 96.4 to 99.3 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 7 went out of service at 0750 on 04 June for turbine rehab.

    - Unit 8 has remained out of service for turbine rehab since 12 September 2006.

    - Unit 10 was run, out of unit priority, at 1300 on 07 June for an electrical inspection.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 1111 on 03 June until 1621 on 04 June due to water in the turbine bearing.  WS was put into one fish unit operation.

    - F1 had reduced loading for lamprey passage studies from:

2200 on 05 June until 0405 on 06 June

2154 on 07 June until 0420 on 08 June

    - F2 had reduced loading for lamprey passage studies from:

2200 on 03 June until 0405 on 04 June

2200 on 05 June until 0405 on 06 June

2154 on 07 June until 0420 on 08 June

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this week:

    - FV1-1 was closed for cleaning from 1525 until 1535 on 07 June.

  - STS/VBS Inspections.  No STS/VBS inspections this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11-18 | NA | NA | NA |

  - Dewatering and Fish Salvage.  The following dewatering and fish salvage activities occurred this week.

    - On 05 June, biologists removed six sturgeon and three lamprey from the U7 draft tube.

    - On 08 June, biologists removed one carp, one bass, six juvenile steelhead, eight sub yearling chinook, eight yearling chinook, six crayfish and one sculpin from the U7 scroll case.

- RESEARCH

  - Battelle spillway survival.  Releasing yearling chinook in the main dam forebay to evaluate survival.

  - CTUIR- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for broodstock purposes.

  - CTWS- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for ceremonial purposes.

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility.

  - NOAA- Ferguson.  B2CC detection evaluation underway.

  - NOAA.  Tagging juvenile yearling chinook at the Smolt Monitoring Facility.

  - NOAA Lamprey.  Tagging of lamprey for LPS and UI continue.

  - PSMFC Smolt Monitoring.  Four steelhead fallback were observed crossing the separator bars.   Three large scale suckers were collected for Bradford Island Remedial Investigations .  200 yearling chinook and steelhead examined for GBT.  2.5% had GBT symptoms. See: http://www.fpc.org/CurrentDaily/Gbtsum.txt.

  - University of Idaho- lamprey.  Block study for lamprey entrance evaluations at WS began on 01 June.

  - University of Idaho- salmon.  Sampling for S. Fork Salmon chinook continues.

  - USACE TDG.  New TDG monitors were installed in the spillway tailrace.

  - USDA Wildlife Services.  Avian hazing began on 07 May.

  - USGS.  Lamprey will be removed from the FERL on 08 June.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

- FISHWAYS

  - Project biologists inspected daily from 03 through 09 June.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |  |
| --- | --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |  |
| 6/3, 6/6-8 | B-branch | FG3-23 incorrect | Unknown | Electricians working on the diffuser. |  |  |
| 6/5 | B-branch | FG3-24 and FG3-25 closed | Unknown | Operator adjusted |  |  |
| 6/6, 6/7 | B-branch weir | Reading <1.3’ | FV3-9 a little low. | Operators adj. FV3-9 |  |  |
| Once | Calibration | Check not done | KW not yet trained. | Training scheduled 6/13 |  |  |
| CASCADES ISLAND |  |  |  |  |  |  |
| 6/7-9 | FG6-10 | Closed | Shaft and motor have parted ways. | TR submitted. See 4.2.6 |  | 07-37350 |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |  |
| WASHINGTON SHORE |  |  |  |  |  |  |
| All week | 11A-S | Closed | Broken shaft | Mech. working on it. |  | 07-40917 |
| 6/3-4 | NUE | Differential low. | F1 OOS. WS in 1 FU operation. | Returned to normal on 6/4 |  |  |
| All week | DSM2 | Screen cleaner #1 in manual |  | Mechanics working on it. |  |  |
| 6/4- | DSM2 | 12C-S light fixture broken | Unknown | TR submitted. |  |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.  Gear box work will begin the week of 11 June.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 6/3 | 62.1 | 62.1 |
| 6/4 | 62.5 | 62.5 |
| 6/5 | 62.4 | 62.4 |
| 6/6 | 61.8 | 61.5 |
| 6/7 | 61.4 | 61.1 |
| 6/8 | 61.8 | 61.6 |
| 6/9 | 62.4 | 62.4 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration will be checked on weekends.

    - B-Branch was put into manual on 2 June.  Cascades Island remains in auto.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - Fish ladders remain in shad passage mode.

    - Main Dam SLEDs are scheduled for removal on 07 June.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - 1C, 3C, and 6C remain set at 70’ msl.

    - DSM1 continues to remain OOS.

    - DSM2 orifice lights are scheduled to be switched back to LEDs on 4 June.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.

  - A teletype sent on 07 June equests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.

JAMES R. MAHAR, P.E.

Operations Manager