### CENWP-OP-B                                                                                                                          02 July 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 26 of 2007, which covers the period from 24 through 30 June 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 166.8 to 205.8 kcfs.  Daily average project tailwater elevation ranged from 14.3’ to 16.9’ msl.  Daily average powerhouse forebay elevation ranged from 72.7’ to 76.3’ msl.  Daily average river temperature ranged from 63 to 64F.  Secchi disk measurements averaged 3.5’ to 6.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 78.8 to 94.2 kcfs.

    - From 1302 until 1337 on 28 June, spill bay 1 was opened to 13’ for debris removal.

    - From 1337 until 1410 on 28 June, spill bay 18 was opened 13’ for debris removal.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 5 has remained out of service for annual maintenance since 11 June.

    - Unit 7 has remained out of service for turbine rehab since 04 June 2007.

    - Unit 8 has remained out of service for turbine rehab since 12 September 2006.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1  and F2 had reduced loading for lamprey passage studies from:

2200 on 24 June until 0400 on 25 June

2200 on 26 June until 0400 on 27 June

2200 on 28 June until 0400 on 30 June

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  No AWS valves were closed this week.

  - STS/VBS Inspections.  The following STS/VBS inspections occurred this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 6/26 | 858 |  |
| 12 | 6/26 | 844 | Repaired A slot |
| 13 | 6/26 | 729 |  |
| 14 | 6/26 | 783 |  |
| 15 | 6/26 | 629 |  |
| 16 | 6/26 | 662 |  |
| 17 | 6/26 | 828 |  |
| 18 | 6/26 | 849 |  |

  - Dewatering and Fish Salvage.  No dewatering and fish salvage activities occurred this week.

- RESEARCH

  - Battelle spillway survival.  Releasing yearling chinook in the main dam forebay to evaluate survival.

  - CRITFC.  Sampling chinook, coho, steelhead and sockeye throughout the season.  Two dead sockeye were reported on 27 June.  Please see memo sent by Fisheries

  - CTUIR- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for broodstock purposes.

  - CTWS- lamprey.  Will receive AFF trapped lamprey from NOAA researchers for ceremonial purposes.

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility.

  - NOAA- Ferguson.  B2CC detection evaluation underway.

  - NOAA- McComas. Tagging juvenile yearling chinook at the Smolt Monitoring Facility.

  - NOAA Lamprey.  Tagging of lamprey for LPS and UI continue.

  - PSMFC Smolt Monitoring.  One salmon fell back over the separator bars.  2806 subyearling chinook were collected for NOAA and Battelle research.  http://www.fpc.org/CurrentDaily/Gbtsum.txt has GBT results.

  - University of Idaho- lamprey.  Block study for lamprey entrance evaluations at WS concluded on 30 June.

  - University of Idaho- salmon.  Sampling for S. Fork Salmon chinook continues.

  - University of Idaho-shad.  Sampling for shad continues.

  - USDA Wildlife Services.  Avian hazing began on 07 May.

  - USGS.  Shad sampling is scheduled to begin 9 July.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

- FISHWAYS

  - Project biologists inspected daily from 24 through 30 June.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 6/28-30 | FG3-4 | Open 30% | Power failure | TR submitted. |  |
| 6/30 | BI weir | Reading <1.1’ | FV3-9 a little low | Operators adj. FV3-9 |  |
| 6/30 | A-branch weir | Reading <1.3’ | FV3-9 a little low | Operators adj. FV3-9 |  |
| 6/28-30 | B-branch weir | Reading <1.3’ | FV3-9 a little low. | Operators adj. FV3-9 |  |
| 6/30 | FG3-24 | Incorrect position for tailwater. | Unknown | Operators closed the diffuser. |  |
| CASCADES ISLAND |  |  |  |  |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| All week | DSM2 | SC #1, #2 in manual | Broken. | Waiting on mechanical parts. |  |
| All week | DSM2 | Add-in/ orifices | Unknown | See 4.6.4 and 7.9 |  |
| All week | DSM2 | Screens 3, 6 and 9 not working. | Bad controls. | Will replace during winter maintenance. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average |
| --- | --- | --- |
| 6/24 | 63.3 | 63.3 |
| 6/25 | 63.4 | 63.3 |
| 6/26 | 63.7 | 63.5 |
| 6/27 | 64.1 | 64.2 |
| 6/28 | 64.5 | 64.4 |
| 6/29 | 64.9 | 64.6 |
| 6/30 | 65.3 | 65.3 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 24 June.  All sensors are out of calibration.  A work order was submitted on 22 June.  WO#07-48294.

    - B-Branch and Cascades Island are in manual.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - Fish ladders remain in shad passage mode.

    - At 1930 on 28 June, FG3-4 had a power failure alarm.  The diffuser is only open 30%.  A TR has been submitted.

  - Juvenile Fishways.

    - PH1 chaingates 1A and 1B remain closed at this time.

    - 1C, 3C, and 6C remain set at 70’ msl.

    - DSM1 remains OOS.

    - DSM2 has experienced high water levels this reporting week.  At 2300 on 26 June, the Add-in was reduced to 30% (12cfs) to keep the ERG from tripping at a high channel elevation.  The Add-in was closed at 0157 on 27 June.  The channel elevation was at 76.5’msl.

      - From 1305 until 1351 on 27 June, the ERG was intentionally tripped so the screens could be inspected.  Screen #3 was found to be completely occluded with debris.  The screen was hand cleaned.  When the channel returned to service, the Add-in was set at 50%.

      - At 0800 on 28 June, the Add-in was adjusted to 25%.

      - At 1909 on 28 June, the Add-in was adjusted to 50%.

      - At 2200 on 28 June, the Add-in was adjusted to 48%.

      - Please see the memo for the record sent by Project Fisheries.

  - Lamprey Fishways.

    - The Bradford Island lamprey ramp remains in service.

    - Washington Shore NDE lamprey ramp was put into service on 29 May.

    - The Washington shore FV6-9 lamprey ramp was put into service on 18 June.

- CONSTRUCTION

  - B1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - PH1 STS/VBS removal and TIES removal.  Six TIES and 23PH1 STSs/VBSs will be scrapped.

  - PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.

- HAZMAT, SPILLS AND CLEANUP.  Nothing to report.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 06 April requests juvenile spill start at 0001 on 10 April.  Bonneville will spill 100K 24 hours a day.  The spill table may be found in the 1007 FPP page Bon-51, Table Bon-15.  At no time will the project voluntarily spill above the 120% gas cap.

  - A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.

  - A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.

  - A teletype sent on 19 June requests a soft forebay constraint of 71.5’ – 72.5’ msl from 0900 until 1800 on 23 June and from 0900 until 1200 on 24 June.  This operation is to allow a work party to stockpile debris on the kite board stating area to provide safer kiteboarder conditions.

  - A teletype sent on 20 June details the start of summer spill for juvenile fish passage.  It supercedes the teletype sent on 06 April (see 7.1).

    - From 0001 on 21 June until 2400 on 15 July, Bonneville will spill 85K during daytime hours using the spill pattern provided by Dennis Schwartz, labeled “Bonneville Spill Patterns- 50-100kcfs”.  Bonneville will spill to the gas cap at night.  Refer to the 2007 FPP, page BON-14 Table BON-6 for daytime hours.

    - From 0001 on 16 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours, using the spill pattern provided by Dennis Schwartz, and to the gas cap at night.

    - If it is necessary to spill above 110kcfs, the Control Room will use the spill pattern found in the 1007 FPP page Bon-51, Table Bon-15.

    - At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”.

    - At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

  - A teletype sent on 20 June requests spill bays 2-17 be on seal  from 1200 until NLT 1600 on 24 June.  Bays 1 and 18 will remain open .5’ to maintain adult fishway attraction flows.  This operation is needed to perform a hydrosurvey in the main dam stilling basin.

  - A teletype sent on 22 June requests that Bonneville forebay be operated with a hard constraint of 75.0’ to 76.5’ and a soft constraint of 75.5’ to 76.5’ from 0600 on 26 June until 1800 on 29 June and from 0600 on 03 July to 1800 on 06 July.  This will help reduce wear and tear on tribal gill net equipment.

  - A teletype sent on 28 June requests the Project flush debris from bays 1 and 18.  Each flushing operation is to last no more than 30 minutes.

  - A teletype sent on 28 June requests a Bonneville forebay soft constraint of 73.5 to 74.5’ msl from 0600 on 30 June to 1200 on 02 July.  This operation is to help prevent the DSM2 ERG from tripping over the weekend.

JAMES R. MAHAR, P.E.

Operations Manager