### CENWP-OP-B                                                                                                                       13 August 2007

MEMORANDUM FOR CENWP-OP, ATTN: Operations Biologist

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for Week 32 of 2007, which covers the period from 05 through 11 August 2007.

- OPERATION SUMMARY

  - Daily average river flows ranged from 137.4 to 163.8 kcfs.  Daily average project tailwater elevation ranged from 12.4’ to 14.4’ msl.  Daily average powerhouse forebay elevation ranged from 73.5’ to 74.6’ msl.  Daily average river temperature ranged from 70 to 71F.  Secchi disk measurements averaged 4.5’ to 7.0’.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and B-Branch respectively, are included in the spill pattern.  Daily average spill ranged from 91.0 to 98.4 kcfs.

  - Unit Operation. Powerhouse 2 is the priority powerhouse.

    - Unit 6 has remained out of service for bank 5/6 maintenance since 30 July.

    - Unit 7 has remained out of service for turbine rehab since 04 June 2007.

    - Unit 8 has remained out of service for turbine rehab since 12 September 2006.

    - Unit 10 was out of service from 0025 on 6 August until 1654 on 9 August for bank 9/10 maintenance.

    - Unit 11 was out of service from 0947 until 1021 on 8 August due to no VBS installed.

    - Unit 12 was out of service from 0330 on 9 August until 1616 on 10 August for governor calibration.

    - Unit 13 was out of service from 0400 until 1539 on 8 August for governor calibration.  U13 had a 1% violation at 0505 on 9 August due to speed adjustment equipment failure.

    - Unit 14 was out of service from 0330 until 1402 on 9 August for governor calibration.  U14 was out of service from 1331 until 1656 on 10 August for model testing.

    - Unit 15 has remained out of service since 09 July for exciter replacement.

    - Unit 16 out of service from 0400 until 1358 on 8 August for governor calibration.  U16 was out of service from 0736 until 0842 for model testing.

    - Unit 17 was out of service from 0844 until 1653 on 7 August for governor calibration.  U17 had a 1% violation at 1640 on 7 August due to governor calibration work.  U17 was out of service from 1223 until 1333 on 11 August for model testing.

    - Unit 18 was out of service from 0440 on 6 August until 0835 on 7 August for governor calibration.  U18 had a 1% violation at 0825 on 7 August due to governor calibration work.  U18 was out of service from 1609 until 1622 on 11 August for model testing.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby, as necessary, during nighttime hours to float debris.

    - F1 was out of service from 0640 until 1650 on 6 August for governor calibration.

    - F2 was out of service from 0410 until 1600 on 7 August for governor calibration.

    - F1 and F2 had reduced loading for lamprey passage studies from:

2200 on 04 August until 0400 on 05 August; 2150 on 05 August until 0400 on 06 August;

2230 on 08 August until 0430 on 09 August; 2200 on 10 August until 0430 on 11 August;

2200 on 11 August

  - Gatewell drawdowns are measured on Wednesdays; VBS drawdowns are measured daily on modified units.

- ACTIVITIES

  - AWS Closures.  The following AWS valves were closed this week:

    - FV3-7 closed for cleaning- from 1602 until 1639 on 8 August; from 0658 until 0721 on 9 August.

    - FV3-9 closed for cleaning- from 1602 until 1639 on 8 August.

  - STS/VBS Inspections.  STS/VBS inspections occurred this week.

Table 1.  STS and VBS inspections.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 12 | 8/6 |  | STSs in manual for inspection from 0722 until 0806 |
| 13 | 8/6 |  | STSs in manual for inspection from 0806 until 0831 |
| 15 | 8/6 |  | STSs in manual for inspection from 0831 until 0906 |
| 16 | 8/6 |  | STSs in manual for inspection from 0906 until 0930 |

  - Dewatering and Fish Salvage.  No dewatering and fish salvage activities occurred this week.

- RESEARCH

  - CRITFC.  Due to temperatures exceeding 70F, sampling is restricted to once a week.

  - CTUIR- lamprey.  Lamprey sampling has resumed due to temperatures dropping to 71.5F on 7 August.

  - NOAA-Gilbreath.  Salt water rearing at the Smolt Monitoring Facility.

  - NOAA- Ferguson.  B2CC detection evaluation continues.

  - NOAA Lamprey.  Lamprey tagging for LPS and UI resumed due to temperatures dropping to 71.5F on 7 August.

  - PSMFC Smolt Monitoring.  No fallbacks crossed the separator bars.  96 shad were collected for USGS.  SbyC continues.  Modified sampling due to temperatures exceeding 70F.

  - University of Idaho- lamprey.  Block study for lamprey entrance evaluations at WS continues.

  - USDA Wildlife Services.  Avian hazing continues.

  - USGS – shad.   Collected 30 adult shad and 66 juvenile shad from the SMF.

  - WDFW Fish Counting.  Visual counting continues Bradford Island and Washington Shore

- FISHWAYS

  - Project biologists inspected daily from 05 through 11 August.  NOAA Fisheries inspected on 10 August.

  - Fish Passage Plan Observations.

Table 2.  FPP Out of Criteria items.

| DATE | ##### LOCATion | ##### FPP itEMS | ##### CAUSE | ##### RESPONSE | ##### TR# |
| --- | --- | --- | --- | --- | --- |
| BRADFORD ISLAND AND BRANCHES |  |  |  |  |  |
| 8/5 | PH1 PCC | Diff. low | System in manual | Operators corrected. |  |
| CASCADES ISLAND |  |  |  |  |  |
| 8/9 | UMT Weir | Reading <1.3’> | Unknown | Operators adjusted. |  |
| All week | FG6-14 | ½ way open | Electricians need to do some rewiring. | Electricians and riggers working out scheduling. |  |
| WASHINGTON SHORE |  |  |  |  |  |
| 8/5-10 | Weir 38 | Reading <1.3’ | Unknown. | No action taken. |  |
| All week | DSM2 Airburst | Screens 3, 6 and 9 not consistent. | Bad controls. | Will replace during winter maintenance. |  |

    - PH1 electronic velocity meter is in an eddy.  Due to this placement, the velocity meter reads less than 1.5 fps.  Readings to meet FPP criteria are taken from the south end mechanical meter.

    - PH1 PCC diffusers FG2-22A and FG2-19 are closed or partially open.  Repairs scheduled for 07/08.

    - FG3-3 stuck partially open.  Repairs are scheduled for winter 07/08.  TR#07-2660

    - FG3-5 has a damaged shaft and the valve won’t operate.  Repairs are scheduled for winter 07/08.

    - FG3-6 stuck partially open.  Repairs are scheduled for winter 07/08.

    - FG6-10 closed.  The motor was repaired on 15 August.  The shaft and gate have parted ways, however and the diffuser will not be operational until repaired in winter 07/08.  Only out of criteria when tailwater is above 19.0’ msl.

  - Fishway Temperatures.  Measurements are taken three weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore. Temperatures are in Fahrenheit.

Table 3.  Bonneville Fishway Temperatures.

| Date | WS average | BI average | AFF average | JMF average |
| --- | --- | --- | --- | --- |
| 8/5 | 71.6 | 71.4 | 71.7 | 70.7 |
| 8/6 | 71.3 | 71.2 | 71.3 | 70.4 |
| 8/7 | 70.7 | 70.4 | 70.7 | 69.9 |
| 8/8 | 70.5 | 70.3 | 70.5 | 69.6 |
| 8/9 | 70.4 | 70.1 | 70.5 | 69.6 |
| 8/10 | 70.4 | 70.1 | 70.4 | 69.4 |
| 8/11 | 70.5 | 70.2 | 70.5 | 69.5 |

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

  - Adult Fishways.

    - Calibration was checked on 11 August.

    - B-Branch and Cascades Island are in manual.

    - FV3-7 is in manual until the A-Branch diffusers are repaired and operating correctly.

    - Fish ladders remain in shad passage mode.

    - Governor testing to occur on all PH2 units from 06-10 August.

  - Juvenile Fishways.

    - On 02 August, the ITS was returned to normal configuration.  Chaingates 1C, 3C, and 6C were open at 70.0’msl.  This is to facilitate the removal of screens from Windy Welders.  The barge relocated to the north end of the powerhouse to unload the fish screens from trucks.  Anticipated return to the south end of the powerhouse, and the start of crane demolition, is 13 August.

    - Due to barge movement and relocation, the ITS was closed at the following times:

0737 until 1417 on 6 August.

0702 until 0730 on 9 August.

    - DSM1 remains OOS.

    - DSM2 screen cleaner 2 went out of service at 1845 on 9 August.  Mechanics repaired the broken chain.  Electricians will need to work on the limit switch.

  - Lamprey Fishways.

    - All lamprey passage structures remain in service.

- CONSTRUCTION

  - PH1 STS/VBS removal.  23 PH1 STSs/VBSs have been scrapped.  Work started on 24 July.

  - PH1 ITS Wall Removal.  Plans are to remove the wall, slope the floor, and install three automated gates.

  - Bradford Island fish exit dredging.  Sediment sampling and sounding occurred on 31 July.

  - Bradford Island clean-up.  Removal of contaminated sediment scheduled to occur in October 2008.  Pre-removal sampling will occur in September.

  - PH2 VBS mods.  Units 14 and 18 are scheduled for winter 07/08.  U17 VBS monitoring equipment will be installed at this time as well.

- HAZMAT, SPILLS AND CLEANUP.

  - On 07 August at 1641 hours, during the daily rounds it was noted that the Powerhouse 1 Oil Water Separator was reading 07 ppm.  This was up from a 04 ppm reading on the previous day.  The NPDES permit threshold is 10 ppm and the system alarms at 08 ppm.  A non-scheduled clean-up of the filters was performed and at approximately 5:20, an oil sheen was discovered and reported.  Upon the initial investigation, it was discovered the return oil pump for Main Unit 6 was under clearance and oil overflowed into the turbine pit resulting in oil pumped into the oil water separator.  It was determined and reported that up to eight gallons of oil entered the river.  The release issue was immediately stopped but the investigation as to the cause and sequence of events continues.

- TELETYPES AND OTHER NOTEWORTHY ITEMS

  - A teletype sent on 21 May requests that the Washington shore adult ladders be reduced to 0.5 feet head from 2200 until 0400 hours for a lamprey test running from 2 June until 1 October.

  - A teletype sent on 07 June requests that all Lower Snake and Columbia River FCRPS projects operate all turbine units within the 1% best efficiency standard during the best efficiency operating period (April 1 through October 31).  Operation outside of 1% is allowed for maintenance, start up/shut down and other instances as outlined in the Fish Passage Plan.  Operation outside of 1% is NOT allowed for any other reason unless a power emergency has been declared.

  - A teletype sent on 20 June details the start of summer spill for juvenile fish passage.

    - From 0001 on 21 June until 2400 on 15 July, Bonneville will spill 85K during daytime hours using the spill pattern provided by Dennis Schwartz, labeled “Bonneville Spill Patterns- 50-100kcfs”.  Bonneville will spill to the gas cap at night.  Refer to the 2007 FPP, page BON-14 Table BON-6 for daytime hours.

    - From 0001 on 16 July until 2400 on 31 August, Bonneville will spill 75K during daytime hours, using the spill pattern provided by Dennis Schwartz, and to the gas cap at night.

    - If it is necessary to spill above 110kcfs, the Control Room will use the spill pattern found in the 1007 FPP page Bon-51, Table Bon-15.

    - At no time will the Project voluntarily spill above the 120% gas cap.  The 120% spill cap level for Bonneville can be found in the teletype “SPILL PRIORITY LIST”.

    - At all times, maintain a minimum generation of 30kcfs and minimum spill of 50kcfs.

  - A teletype sent on 19 July provides guidance on project operation to provide voluntary and involuntary spill.  The teletype provided spill order by project, as well as spill caps for various TDG levels.

JAMES R. MAHAR, P.E.

Operations Manager